## Annual Summary 12-13
2012-2013 FUEL & ELECTRICTY CONSUMPTION (FOR MAIN METERS ONLY)
|  | JUNE | JULY | AUGUST | SEP | OCT | NOV | DEC | JAN | FEB | MARCH | APRIL | MAY | YTD TOTAL
GAS | QUANTITY-MCF | 0 | 0 | 0 | 622 | 6898 | 9891 | 13579 | 14777 | 10241 | 10533 | 8624 | 2745 | 77910
| COST-$ | 311.17 | 311.17 | 311.17 | 2573 | 28322 | 46004.53 | 63048 | 63343 | 43982 | 45910 | 43192 | 14660 | 351968.04
| UNIT COST | 0 | 0 | 0 | 4.1367 | 4.1058 | 4.6512 | 4.6431 | 4.2866 | 4.2947 | 4.3587 | 5.0083 | 5.3406 | 4.5176
| MCF BTUS (x 1000) | 0 | 0 | 0 | 622000 | 6898000 | 9891000 | 13579000 | 14777000 | 10241000 | 10533000 | 8624000 | 2745000 | 77910000
#2 FUEL OIL | QUANTITY-GAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| COST-$ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| UNIT COST | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BTUS (x 1000) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
#6 FUEL OIL | QUANTITY-GAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11098 | 18234 | 0 | 0 | 29332
| COST-$ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16314 | 25527 | 0 | 0 | 41841
| UNIT COST | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.47 | 1.4 | 0 | 0 | 0
| BTUS (x 1000) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1664700 | 2735100 | 0 | 0 | 4399800
TOTAL HEATING BTU | QTY-BTU (x 1000) | 0 | 0 | 0 | 622000 | 6898000 | 9891000 | 13579000 | 14777000 | 11905700 | 13268100 | 8624000 | 2745000 | 82309800
TOTAL HEATING COSTS |  | 311.17 | 311.17 | 311.17 | 2573 | 28322 | 46004.53 | 63048 | 63343 | 60296 | 71437 | 43192 | 14660 | 393809.04
ELECTRICITY | QUANTITY-KWH | 739200 | 850500 | 688800 | 907200 | 915600 | 1026900 | 1047900 | 945000 | 1043700 | 957600 | 995400 | 816900 | 10934700
(125 Snelling Ave S - Main Meter) | # BILLING DAYS | 30 | 32 | 28 | 31 | 29 | 33 | 33 | 30 | 29 | 29 | 31 | 31 | 366
| KWH PER DAY | 24640 | 26578.125 | 24600 | 29264.5161 | 31572.4138 | 31118.1818 | 31754.5455 | 31500 | 35989.6552 | 33020.6897 | 32109.6774 | 26351.6129 | 29876.2295
| COST-$ | 58865 | 68584 | 56706 | 74701 | 71060 | 74353.36 | 76113 | 71828 | 81620 | 74036 | 78727 | 73072 | 859665.36
| UNIT COST | 0.079633 | 0.08064 | 0.082326 | 0.082342 | 0.07761 | 0.072406 | 0.072634 | 0.076008 | 0.078203 | 0.077314 | 0.079091 | 0.08945 | 0.078618
Peak Demand (per Xcel billing) | QUANTITY KW | 1578 | 1722 | 1497 | 1743 | 1911 | 1890 | 1848 | 1764 | 1932 | 1827 | 1911 | 1890 | 1792.75
Peak Demand (per Xcel billing) | COST - $ | 14402 | 16497 | 14341 | 19102 | 15566 | 14156.1 | 13842 | 13212 | 14471 | 13684 | 14313 | 14156 | 177742.1
| BTUS (x 1000) | 2522150.4 | 2901906 | 2350185.6 | 3095366.4 | 3124027.2 | 3503782.8 | 3575434.8 | 3224340 | 3561104.4 | 3267331.2 | 3396304.8 | 2787262.8 | 37309196.4 | 0
ELECTRICITY | QUANTITY-KWH | 173600 | 343000 | 177800 | 138600 | 32200 | 8400 | 11200 | 8400 | 14000 | 14000 | 9800 | 50400 | 981400
(85 Snelling Ave S - Chiller Plant) | # BILLING DAYS | 30 | 32 | 28 | 31 | 29 | 33 | 33 | 30 | 29 | 29 | 31 | 31 | 366
| KWH PER DAY | 5786.6667 | 10718.75 | 6350 | 4470.9677 | 1110.3448 | 254.5455 | 339.3939 | 280 | 482.7586 | 482.7586 | 316.129 | 1625.8065 | 2681.4208
| COST-$ | 22245 | 33798 | 23722 | 16628 | 7086 | 1176.17 | 1290 | 1319 | 1508 | 1631 | 1265 | 8465 | 120133.17
| UNIT COST | 0.12814 | 0.098536 | 0.13342 | 0.11997 | 0.22006 | 0.14002 | 0.11518 | 0.15702 | 0.10771 | 0.1165 | 0.12908 | 0.16796 | 0.12241
Peak Demand (per Xcel billing) | QUANTITY KW | 1054 | 1136 | 1091 | 648 | 535 | 76 | 68 | 80 | 60 | 75 | 66 | 488 | 5377
Peak Demand (per Xcel billing) | COST - $ | 9620 | 10883 | 709 | 7102 | 4445 | 569.24 | 509 | 599 | 449 | 562 | 494 | 3655 | 39596.24
| BTUS (x 1000) | 592323.2 | 1170316 | 606653.6 | 472903.2 | 109866.4 | 28660.8 | 38214.4 | 28660.8 | 47768 | 47768 | 33437.6 | 171964.8 | 3348536.8
Total Electricity | QUANTITY-KWH | 912800 | 1193500 | 866600 | 1045800 | 947800 | 1035300 | 1059100 | 953400 | 1057700 | 971600 | 1005200 | 867300 | 11916100
| UNIT COST | 0.088858 | 0.085783 | 0.092809 | 0.087329 | 0.08245 | 0.072954 | 0.073084 | 0.076722 | 0.078593 | 0.077879 | 0.079578 | 0.094012 | 0.082225
| COST-$ | 81110 | 102382 | 80428 | 91329 | 78146 | 75529.53 | 77403 | 73147 | 83128 | 75667 | 79992 | 81537 | 979798.53
TOTAL CAMPUS BTU CONSUMPTION x 1 MIL |  | 3114.4736 | 4072.222 | 2956.8392 | 4190.2696 | 10131.8936 | 13423.4436 | 17192.6492 | 18030.0008 | 15514.5724 | 16583.1992 | 12053.7424 | 5704.2276 | 122967.5332
# STEAM GENERATED |  | 0 | 0 | 0 | 383000 | 5746000 | 7934000 | 10943000 | 12697000 | 9839077 | 9433891 | 7604590 | 2523000 | 67103558
BOILER EFFICIENCY (BTU STEAM/BTU FUEL) |  | 0% | 0% | 0% | 54.43% | 73.64% | 70.91% | 71.24% | 75.96% | 73.06% | 62.85% | 77.95% | 81.25% | 80.16%
HEATING DEGREE DAY - ACTUAL (MAC) |  | 0 | 2 | 40 | 107 | 515 | 811 | 1222 | 1430 | 1258 | 1161 | 756 | 260 | 7562
COOLING DEGREE DAY - ACTUAL (MAC) |  | 277 | 438 | 271 | 148 | 8 | 0 | 0 | 0 | 0 | 0 | 13 | 87 | 1242
Chiller #1 Run Time |  | 344 | 214 | 62 | 138 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 832
Chiller #2 Run Time |  | 104 | 528 | 4 | 150 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 945
Chiller #3 Run Time |  | 245 | 73 | 551 | 37 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 925
2011-2012 FUEL & ELECTRICTY CONSUMPTION (FOR MAIN METERS ONLY)
|  | JUNE | JULY | AUGUST | SEP | OCT | NOV | DEC | JAN | FEB | MARCH | APRIL | MAY | YTD TOTAL
GAS | QUANTITY-MCF | 0 | 0 | 0 | 119 | 4726 | 9983 | 12738 | 12291 | 11934 | 6124 | 5408 | 1268 | 64591
| COST-$ | 311.17 | 311.17 | 311.17 | 921 | 24175 | 52924.13 | 66790 | 60419 | 56345 | 28973 | 20384.2 | 4172 | 316036.84
| UNIT COST | 0 | 0 | 0 | 7.7395 | 5.1153 | 5.3014 | 5.2434 | 4.9157 | 4.7214 | 4.7311 | 3.7693 | 3.2902 | 4.8929
| MCF BTUS (x 1000) | 0 | 0 | 0 | 119000 | 4726000 | 9983000 | 12738000 | 12291000 | 11934000 | 6124000 | 5408000 | 1268000 | 64591000
#2 FUEL OIL | QUANTITY-GAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| COST-$ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| UNIT COST | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BTUS (x 1000) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
#6 FUEL OIL | QUANTITY-GAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| COST-$ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| UNIT COST | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BTUS (x 1000) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TOTAL HEATING BTU | QTY-BTU (x 1000) | 0 | 0 | 0 | 119000 | 4726000 | 9983000 | 12738000 | 12291000 | 11934000 | 6124000 | 5408000 | 1268000 | 64591000
TOTAL HEATING COSTS |  | 311.17 | 311.17 | 311.17 | 921 | 24175 | 52924.13 | 66790 | 60419 | 56345 | 28973 | 20384.2 | 4172 | 316036.84
ELECTRICITY | QUANTITY-KWH | 571200 | 630000 | 621600 | 732900 | 814800 | 890400 | 1056300 | 911400 | 1016400 | 919800 | 1016400 | 716100 | 9897300
(125 Snelling Ave S - Main Meter) | # BILLING DAYS | 29 | 30 | 30 | 31 | 29 | 29 | 35 | 31 | 30 | 29 | 33 | 28 | 364
| KWH PER DAY | 19696.5517 | 21000 | 20720 | 23641.9355 | 28096.5517 | 30703.4483 | 30180 | 29400 | 33880 | 31717.2414 | 30800 | 25575 | 27190.3846
| COST-$ | 47693 | 52555 | 50178 | 61585 | 60368 | 58715.25 | 73828 | 66606 | 70055 | 67251 | 68179.04 | 51940 | 728953.29
| UNIT COST | 0.083496 | 0.083421 | 0.080724 | 0.084029 | 0.074089 | 0.065943 | 0.069893 | 0.073081 | 0.068925 | 0.073115 | 0.067079 | 0.072532 | 0.073652
Peak Demand (per Xcel billing) | QUANTITY KW | 1245 | 1393 | 1231 | 1575 | 1764 | 1827 | 1827 | 1785 | 1848 | 1848 | 1827 | 1688 | 1654.8333
Peak Demand (per Xcel billing) | COST - $ | 11636 | 13345 | 11793 | 15089 | 11729 | 11290.86 | 11291 | 11031 | 11421 | 11421 | 11290.86 | 10432 | 141769.72
| BTUS (x 1000) | 1948934.4 | 2149560 | 2120899.2 | 2500654.8 | 2780097.6 | 3038044.8 | 3604095.6 | 3109696.8 | 3467956.8 | 3138357.6 | 3467956.8 | 2443333.2 | 33769587.6 | 0
ELECTRICITY | QUANTITY-KWH | 240800 | 383600 | 357000 | 242200 | 148400 | 28000 | 23800 | 18200 | 9800 | 11200 | 9800 | 84000 | 1556800
(85 Snelling Ave S - Chiller Plant) | # BILLING DAYS | 29 | 30 | 31 | 30 | 29 | 29 | 35 | 31 | 30 | 29 | 33 | 28 | 364
| KWH PER DAY | 8303.4483 | 12786.6667 | 11516.129 | 8073.3333 | 5117.2414 | 965.5172 | 680 | 587.0968 | 326.6667 | 386.2069 | 296.9697 | 3000 | 4276.9231
| COST-$ | 27028 | 43209 | 34332 | 28186 | 16054 | 3940.39 | 3213 | 2660 | 1447 | 1701 | 1332.91 | 11919 | 175022.3
| UNIT COST | 0.11224 | 0.11264 | 0.096168 | 0.11637 | 0.10818 | 0.14073 | 0.135 | 0.14615 | 0.14765 | 0.15188 | 0.13601 | 0.14189 | 0.11242
Peak Demand (per Xcel billing) | QUANTITY KW | 1059 | 1713 | 1094 | 1109 | 857 | 290 | 204 | 176 | 98 | 116 | 89 | 857 | 7662
Peak Demand (per Xcel billing) | COST - $ | 9897 | 16411 | 10481 | 10624 | 5698 | 1792.2 | 1261 | 1088 | 606 | 717 | 550.02 | 5296 | 64421.22
| BTUS (x 1000) | 821609.6 | 1308843.2 | 1218084 | 826386.4 | 506340.8 | 95536 | 81205.6 | 62098.4 | 33437.6 | 38214.4 | 33437.6 | 286608 | 5311801.6
Total Electricity | QUANTITY-KWH | 812000 | 1013600 | 978600 | 975100 | 963200 | 918400 | 1080100 | 929600 | 1026200 | 931000 | 1026200 | 800100 | 11454100
| UNIT COST | 0.092021 | 0.094479 | 0.086358 | 0.092063 | 0.079342 | 0.068223 | 0.071328 | 0.074512 | 0.069676 | 0.074062 | 0.067737 | 0.079814 | 0.078922
| COST-$ | 74721 | 95764 | 84510 | 89771 | 76422 | 62655.64 | 77041 | 69266 | 71502 | 68952 | 69511.95 | 63859 | 903975.59
TOTAL CAMPUS BTU CONSUMPTION x 1 MIL |  | 2770.544 | 3458.4032 | 3338.9832 | 3446.0412 | 8012.4384 | 13116.5808 | 16423.3012 | 15462.7952 | 15435.3944 | 9300.572 | 8909.3944 | 3997.9412 | 103672.3892
# STEAM GENERATED |  | 0 | 0 | 0 | 0 | 0 | 0 | 10296000 | 11218000 | 9766000 | 6132000 | 4996000 | 1328000 | 43736000
BOILER EFFICIENCY (BTU STEAM/BTU FUEL) |  | 0% | 0% | 0% | 0% | 0% | 0% | 71.45% | 80.68% | 72.34% | 88.52% | 81.67% | 92.58% | 60.91%
HEATING DEGREE DAY - ACTUAL (MAC) |  | 72 | 2 | 21 | 196 | 392 | 797 | 1151 | 1281 | 1074 | 530 | 444 | 142 | 6102
COOLING DEGREE DAY - ACTUAL (MAC) |  | 178 | 395 | 266 | 101 | 69 | 0 | 0 | 0 | 0 | 32 | 15 | 121 | 1177
Chiller #1 Run Time |  | 120 | 237 | 222 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 104 | 701
Chiller #2 Run Time |  | 374 | 287 | 175 | 147 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 1208
Chiller #3 Run Time |  | 51 | 339 | 322 | 172 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 1053
Note on H99: macalester: Estimated reading, meter not recording since O2 trim installed (no IP address)

## Summary page breaks
2012-2013 FUEL & ELECTRICTY CONSUMPTION
(FOR MAIN METERS ONLY)
|  | JUNE | JULY | AUGUST | SEP | OCT | NOV | DEC | JAN | FEB | MARCH | APRIL | MAY | YTD TOTAL
GAS | QUANTITY-MCF | 0 | 0 | 0 | 622 | 6898 | 9891 | 13579 | 14777 | 10241 | 10533 | 8624 | 2745 | 77910
| COST-$ | 311.17 | 311.17 | 311.17 | 2573 | 28322 | 46004.53 | 63048 | 63343 | 43982 | 45910 | 43192 | 14660 | 351968.04
| UNIT COST | 0 | 0 | 0 | 0 | 4.1058 | 4.6512 | 4.6431 | 4.2866 | 4.2947 | 4.3587 | 5.0083 | 5.3406 | 4.5176
| MCF BTUS (x 1000) | 0 | 0 | 0 | 622000 | 6898000 | 9891000 | 13579000 | 14777000 | 10241000 | 10533000 | 8624000 | 2745000 | 77910000
#2 FUEL OIL | QUANTITY-GAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| COST-$ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| UNIT COST | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BTUS (x 1000) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
#6 FUEL OIL | QUANTITY-GAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11098 | 18234 | 0 | 0 | 29332
| COST-$ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16314 | 25527 | 0 | 0 | 41841
| UNIT COST | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.47 | 1.4 | 0 | 0 | 0
| BTUS (x 1000) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1664700 | 2735100 | 0 | 0 | 4399800
TOTAL HEATING BTU | QTY-BTU (x 1000) | 0 | 0 | 0 | 622000 | 6898000 | 9891000 | 13579000 | 14777000 | 11905700 | 13268100 | 8624000 | 2745000 | 82309800
TOTAL HEATING COSTS |  | 311.17 | 311.17 | 311.17 | 2573 | 28322 | 46004.53 | 63048 | 63343 | 60296 | 71437 | 43192 | 14660 | 393809.04
ELECTRICITY | QUANTITY-KWH | 739200 | 850500 | 688800 | 907200 | 915600 | 1026900 | 1047900 | 945000 | 1043700 | 957600 | 995400 | 816900 | 10934700
(per 121 S Snelling Xcel billing) | # BILLING DAYS | 30 | 32 | 28 | 31 | 29 | 33 | 33 | 30 | 29 | 29 | 31 | 31 | 366
| KWH PER DAY | 24640 | 26578.125 | 24600 | 29264.5161 | 31572.4138 | 31118.1818 | 31754.5455 | 31500 | 35989.6552 | 33020.6897 | 32109.6774 | 26351.6129 | 29876.2295
| COST-$ | 58865 | 68584 | 56706 | 74701 | 71060 | 74353.36 | 76113 | 71828 | 81620 | 74036 | 78727 | 73072 | 859665.36
| UNIT COST | 0.079633 | 0.08064 | 0.082326 | 0.082342 | 0.07761 | 0.072406 | 0.072634 | 0.076008 | 0.078203 | 0.077314 | 0.079091 | 0.08945 | 0.078618
Demand (per 121 S Snelling Xcel billing) | QUANTITY KW | 1578 | 1722 | 1497 | 1743 | 1911 | 1890 | 1848 | 1764 | 1932 | 1827 | 1911 | 1890 | 1792.75
Demand (per 121 S Snelling Xcel billing) | COST - $ | 14402 | 16497 | 14341 | 19102 | 15566 | 14156.1 | 13842 | 13212 | 14471 | 13684 | 14313 | 14156 | 177742.1
| BTUS (x 1000) | 2522150.4 | 2901906 | 2350185.6 | 3095366.4 | 3124027.2 | 3503782.8 | 3575434.8 | 3224340 | 3561104.4 | 3267331.2 | 3396304.8 | 2787262.8 | 37309196.4
ELECTRICITY | QUANTITY-KWH | 173600 | 343000 | 177800 | 138600 | 32200 | 8400 | 11200 | 8400 | 14000 | 14000 | 9800 | 50400 | 981400
(85 S. Snelling - Chiller Plant) | # BILLING DAYS | 30 | 32 | 28 | 31 | 29 | 33 | 33 | 30 | 29 | 29 | 31 | 31 | 366
| KWH PER DAY | 5786.6667 | 10718.75 | 6350 | 4470.9677 | 1110.3448 | 254.5455 | 339.3939 | 280 | 482.7586 | 482.7586 | 316.129 | 1625.8065 | 2681.4208
| COST-$ | 22245 | 33798 | 23722 | 16628 | 7086 | 1176.17 | 1290 | 1319 | 1508 | 1631 | 1265 | 8465 | 120133.17
| UNIT COST | 0.12814 | 0.098536 | 0.13342 | 0.11997 | 0.22006 | 0.14002 | 0.11518 | 0.15702 | 0.10771 | 0.1165 | 0.12908 | 0.16796 | 0.12241
Peak Demand (per Xcel billing) | QUANTITY KW | 1054 | 1136 | 1091 | 648 | 535 | 76 | 68 | 80 | 60 | 75 | 66 | 488 | 5377
Peak Demand (per Xcel billing) | COST - $ | 9620 | 10883 | 709 | 7102 | 4445 | 569.24 | 509 | 599 | 449 | 562 | 494 | 3655 | 39596.24
| BTUS (x 1000) | 592323.2 | 1170316 | 606653.6 | 472903.2 | 109866.4 | 28660.8 | 38214.4 | 28660.8 | 47768 | 47768 | 33437.6 | 171964.8 | 3348536.8
Total Electricity | QUANTITY-KWH | 912800 | 1193500 | 866600 | 1045800 | 947800 | 1035300 | 1059100 | 953400 | 1057700 | 971600 | 1005200 | 867300 | 11916100
| UNIT COST | 0.088858 | 0.085783 | 0.092809 | 0.087329 | 0.08245 | 0.072954 | 0.073084 | 0.076722 | 0.078593 | 0.077879 | 0.079578 | 0.094012 | 0.082225
| COST-$ | 81110 | 102382 | 80428 | 91329 | 78146 | 75529.53 | 77403 | 73147 | 83128 | 75667 | 79992 | 81537 | 979798.53
TOTAL CAMPUS BTU CONSUMPTION x 1 MIL |  | 3114.4736 | 4072.222 | 2956.8392 | 4190.2696 | 10131.8936 | 13423.4436 | 17192.6492 | 18030.0008 | 15514.5724 | 16583.1992 | 12053.7424 | 5704.2276 | 122967.5332
# STEAM GENERATED |  | 0 | 0 | 0 | 383000 | 5746000 | 7934000 | 10943000 | 12697000 | 9839077 | 9433891 | 7604590 | 2523000 | 67103558
BOILER EFFICIENCY (BTU STEAM/BTU FUEL) |  | 0% | 0% | 0% | 54.43% | 73.64% | 70.91% | 71.24% | 75.96% | 73.06% | 62.85% | 77.95% | 81.25% | 80.16%
HEATING DEGREE DAY - ACTUAL (MAC) |  | 0 | 2 | 40 | 107 | 515 | 811 | 1222 | 1430 | 1258 | 1161 | 756 | 260 | 7562
COOLING DEGREE DAY - ACTUAL (MAC) |  | 277 | 438 | 271 | 148 | 8 | 0 | 0 | 0 | 0 | 0 | 13 | 87 | 1242
Chiller #1 Run Time |  | 344 | 214 | 62 | 138 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 832
Chiller #2 Run Time |  | 104 | 528 | 4 | 150 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 945
Chiller #3 Run Time |  | 245 | 73 | 551 | 37 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 925
2011-2012 FUEL & ELECTRICTY CONSUMPTION
(FOR MAIN METERS ONLY)
|  | JUNE | JULY | AUGUST | SEP | OCT | NOV | DEC | JAN | FEB | MARCH | APRIL | MAY | YTD TOTAL
GAS | QUANTITY-MCF | 0 | 0 | 0 | 119 | 4726 | 9983 | 12738 | 12291 | 11934 | 6124 | 5408 | 1268 | 64591
| COST-$ | 311.17 | 311.17 | 311.17 | 921 | 24175 | 52924.13 | 66790 | 60419 | 56345 | 28973 | 20384.2 | 4172 | 316036.84
| UNIT COST | 0 | 0 | 0 | 0 | 5.1153 | 5.3014 | 5.2434 | 4.9157 | 4.7214 | 4.7311 | 3.7693 | 3.2902 | 4.8929
| MCF BTUS (x 1000) | 0 | 0 | 0 | 119000 | 4726000 | 9983000 | 12738000 | 12291000 | 11934000 | 6124000 | 5408000 | 1268000 | 64591000
#2 FUEL OIL | QUANTITY-GAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| COST-$ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| UNIT COST | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0!
| BTUS (x 1000) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
#6 FUEL OIL | QUANTITY-GAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| COST-$ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| UNIT COST | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0!
| BTUS (x 1000) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TOTAL HEATING BTU | QTY-BTU (x 1000) | 0 | 0 | 0 | 119000 | 4726000 | 9983000 | 12738000 | 12291000 | 11934000 | 6124000 | 5408000 | 1268000 | 64591000
TOTAL HEATING COSTS |  | 311.17 | 311.17 | 311.17 | 921 | 24175 | 52924.13 | 66790 | 60419 | 56345 | 28973 | 20384.2 | 4172 | 316036.84
ELECTRICITY | QUANTITY-KWH | 571200 | 630000 | 621600 | 732900 | 814800 | 890400 | 1056300 | 911400 | 1016400 | 919800 | 1016400 | 716100 | 9897300
(per 121 S Snelling Xcel billing) | # BILLING DAYS | 29 | 30 | 30 | 31 | 29 | 29 | 35 | 31 | 30 | 29 | 33 | 28 | 364
| KWH PER DAY | 19696.5517 | 21000 | 20720 | 23641.9355 | 28096.5517 | 30703.4483 | 30180 | 29400 | 33880 | 31717.2414 | 30800 | 25575 | 27190.3846
| COST-$ | 47693 | 52555 | 50178 | 61585 | 60368 | 58715.25 | 73828 | 66606 | 70055 | 67251 | 68179.04 | 51940 | 728953.29
| UNIT COST | 0.083496 | 0.083421 | 0.080724 | 0.084029 | 0.074089 | 0.065943 | 0.069893 | 0.073081 | 0.068925 | 0.073115 | 0.067079 | 0.072532 | 0.073652
Demand (per 121 S Snelling Xcel billing) | QUANTITY KW | 1245 | 1393 | 1231 | 1575 | 1764 | 1827 | 1827 | 1785 | 1848 | 1848 | 1827 | 1688 | 1654.8333
Demand (per 121 S Snelling Xcel billing) | COST - $ | 11636 | 13345 | 11793 | 15089 | 11729 | 11290.86 | 11291 | 11031 | 11421 | 11421 | 11290.86 | 10432 | 141769.72
| BTUS (x 1000) | 1948934.4 | 2149560 | 2120899.2 | 2500654.8 | 2780097.6 | 3038044.8 | 3604095.6 | 3109696.8 | 3467956.8 | 3138357.6 | 3467956.8 | 2443333.2 | 33769587.6
ELECTRICITY | QUANTITY-KWH | 240800 | 383600 | 357000 | 242200 | 148400 | 28000 | 23800 | 18200 | 9800 | 11200 | 9800 | 84000 | 1556800
(85 S. Snelling - Chiller Plant) | # BILLING DAYS | 29 | 30 | 31 | 30 | 29 | 29 | 35 | 31 | 30 | 29 | 33 | 28 | 364
| KWH PER DAY | 8303.4483 | 12786.6667 | 11516.129 | 8073.3333 | 5117.2414 | 965.5172 | 680 | 587.0968 | 326.6667 | 386.2069 | 296.9697 | 3000 | 4276.9231
| COST-$ | 27028 | 43209 | 34332 | 28186 | 16054 | 3940.39 | 3213 | 2660 | 1447 | 1701 | 1332.91 | 11919 | 175022.3
| UNIT COST | 0.11224 | 0.11264 | 0.096168 | 0.11637 | 0.10818 | 0.14073 | 0.135 | 0.14615 | 0.14765 | 0.15188 | 0.13601 | 0.14189 | 0.11242
Peak Demand (per Xcel billing) | QUANTITY KW | 1059 | 1713 | 1094 | 1109 | 857 | 290 | 204 | 176 | 98 | 116 | 89 | 857 | 7662
Peak Demand (per Xcel billing) | COST - $ | 9897 | 16411 | 10481 | 10624 | 5698 | 1792.2 | 1261 | 1088 | 606 | 717 | 550.02 | 5296 | 64421.22
| BTUS (x 1000) | 821609.6 | 1308843.2 | 1218084 | 826386.4 | 506340.8 | 95536 | 81205.6 | 62098.4 | 33437.6 | 38214.4 | 33437.6 | 286608 | 5311801.6
Total Electricity | QUANTITY-KWH | 812000 | 1013600 | 978600 | 975100 | 963200 | 918400 | 1080100 | 929600 | 1026200 | 931000 | 1026200 | 800100 | 11454100
| UNIT COST | 0.092021 | 0.094479 | 0.086358 | 0.092063 | 0.079342 | 0.068223 | 0.071328 | 0.074512 | 0.069676 | 0.074062 | 0.067737 | 0.079814 | 0.078922
Note: 2010 XCEL Elec. Rate Crdts | CREDITS | 74721 | 95764 | 84510 | 89771 | 76422 | 62655.64 | 77041 | 69266 | 71502 | 68952 | 69511.95 | 63859 | 903975.59
| COST-$ | [12 empty] | 903975.59
TOTAL CAMPUS BTU CONSUMPTION x 1 MIL |  | 2770.544 | 3458.4032 | 3338.9832 | 3446.0412 | 8012.4384 | 13116.5808 | 16423.3012 | 15462.7952 | 15435.3944 | 9300.572 | 8909.3944 | 3997.9412 | 103672.3892
# STEAM GENERATED |  | 0 | 0 | 0 | 0 | 0 | 0 | 10296000 | 11218000 | 9766000 | 6132000 | 4996000 | 1328000 | 43736000
BOILER EFFICIENCY (BTU STEAM/BTU FUEL) |  | 0% | 0% | 0% | 0% | 0% | 0% | 71.45% | 80.68% | 72.34% | 88.52% | 81.67% | 92.58% | 81.21%
HEATING DEGREE DAY - ACTUAL (MAC) |  | 72 | 2 | 21 | 196 | 392 | 797 | 1151 | 1281 | 1074 | 530 | 444 | 142 | 6102
COOLING DEGREE DAY - ACTUAL (MAC) |  | 178 | 395 | 266 | 101 | 69 | 0 | 0 | 0 | 0 | 32 | 15 | 121 | 1177
Chiller #1 Run Time |  | 120 | 237 | 222 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 104 | 701
Chiller #2 Run Time |  | 374 | 287 | 175 | 147 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 1208
Chiller #3 Run Time |  | 51 | 339 | 322 | 172 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 1053
Note on H101: macalester: Estimated reading, meter not recording since O2 trim installed (no IP address)

## KWH Consumption
Electricity kwh
Year | June | July | August | September | October | November | December | January | February | March | April | May | Total
1991-92 (10,699,200 kwh) | 789600 | 1024800 | 878400 | 976800 | 873600 | 890400 | 931200 | 724800 | 1027200 | 818400 | 952800 | 811200 | 10699200
1992-93 (10,420,800 kwh) | 715200 | 861600 | 681600 | 876000 | 768000 | 988800 | 912000 | 914400 | 1089600 | 888000 | 957600 | 768000 | 10420800
1993-94 (10,384,173 kwh) | 722400 | 741600 | 782400 | 905013 | 935180 | 896884 | 915796 | 870500 | 1070400 | 825600 | 847200 | 871200 | 10384173
1994-95 (10,454,200 kwh) | 820800 | 763000 | 868800 | 957600 | 686400 | 955200 | 1018286 | 925714 | 981600 | 871200 | 955200 | 650400 | 10454200
1995-96 (10,836,825 kwh) | 840000 | 843200 | 768800 | 792525 | 924000 | 955460 | 987320 | 987320 | 972580 | 972500 | 947890 | 845230 | 10836825
1996-97 (11,988,879 kwh) | 727680 | 1204800 | 691200 | 1070400 | 960000 | 998400 | 1039898 | 1074562 | 1135139 | 1036800 | 972000 | 1078000 | 11988879
1997-98 (12,782,400 kwh) | 940800 | 979200 | 1008000 | 1135200 | 1144800 | 1096800 | 1195200 | 936000 | 1034400 | 1161600 | 1039200 | 1111200 | 12782400
1998-99 (12,979,200 kwh) | 1012800 | 1022400 | 1212000 | 1128000 | 1128000 | 945600 | 1195200 | 1056000 | 1101600 | 1039200 | 1130400 | 1008000 | 12979200
1999-00 (12,117,600 kwh) | 974400 | 1123200 | 1125600 | 1096800 | 1020000 | 1099200 | 849600 | 1020000 | 1039200 | 936000 | 878400 | 955200 | 12117600
2000-01 (11,611,968 kwh) | 960000 | 1058400 | 1468800 | 891072 | 909792 | 876096 | 1096992 | 662688 | 1029600 | 692640 | 1048320 | 917568 | 11611968
2001-02 (12,739,200 kwh) | 1000800 | 1365600 | 924000 | 837600 | 1231200 | 1116000 | 856800 | 1293600 | 926400 | 1094400 | 1243200 | 849600 | 12739200
2002-03 (13,257,600 kwh) | 1056000 | 1262400 | 1020000 | 1329600 | 998400 | 1291200 | 854400 | 1128000 | 1240800 | 976800 | 1101600 | 998400 | 13257600
2003-04 (12,969,000 kwh) | 967200 | 1039200 | 1240800 | 1159200 | 1257600 | 1015200 | 1180800 | 1041600 | 1060800 | 844800 | 1274400 | 888000 | 12969600
2004-05 (12,969,000 kwh) | 899585 | 1105860 | 977142 | 1265510 | 1079949 | 1045310 | 1015844 | 1087376 | 1196023 | 1237149 | 1045415 | 989008 | 12944171
2005-06 (13,058,757 kwh) | 1029339 | 1209515 | 1077824 | 1224364 | 1065547 | 1007698 | 1236344 | 1033577 | 1140243 | 1071488 | 1012501 | 950317 | 13058757
2006-07 (11,177,000 kwh) | 1005600 | 1171200 | 1056000 | 1118400 | 1036800 | 1075200 | 1075200 | 938400 | 1048800 | 1070400 | 959000 | 844200 | 12399200
2007-08 (10,787,257 kwh) | 872200 | 982800 | 890400 | 1080800 | 905800 | 910000 | 996800 | 814800 | 950600 | 848400 | 889000 | 645657 | 10787257
2008-09 (12,337,600 kwh) | 737100 | 1125600 | 1106700 | 1283100 | 942900 | 1033200 | 1106700 | 1001700 | 1155000 | 926200 | 1008000 | 911400 | 12337600
2009-10 (11,670,400 kwh) | 701400 | 1087100 | 866600 | 1066100 | 996800 | 980000 | 1106000 | 1047200 | 1045800 | 980000 | 945000 | 848400 | 11670400
2010-11 (11,887,400 kwh) | 945000 | 1044400 | 983500 | 992600 | 998200 | 1003100 | 1118600 | 1021300 | 1008000 | 968800 | 947800 | 856100 | 11887400
2011-12 (11,454,100 kwh) | 812000 | 1013600 | 978600 | 975100 | 963200 | 918400 | 1080100 | 929600 | 1026200 | 931000 | 1026200 | 800100 | 11454100
2012-13 (11,916,100 kwh) | 912800 | 1193500 | 866600 | 1045800 | 947800 | 1035300 | 1059100 | 953400 | 1057700 | 971600 | 1005200 | 867300 | 11916100
TOTAL | 19442704 | 23222975 | 20607166 | 22161784 | 20826168 | 22133448 | 22828180 | 21462537 | 23337685 | 21162977 | 22186326 | 19464480 | 249780530
5 YEAR AVERAGE | 821660 | 1092840 | 960400 | 1072540 | 969780 | 994000 | 1094100 | 990640 | 1058540 | 955520 | 986440 | 856660 | 11853120

## Electrical Cost
COST | B | C | D | E | F | G |  | H | I | J | K | L | M
ELECTRICITY TOTAL COST
YEAR | JUNE | JULY | AUGUST | SEPTEMBER | OCTOBER | NOVEMBER | DECEMBER | JANUARY | FEBRUARY | MARCH | APRIL | MAY | TOTAL
1989-90 | 40002.4 | 43554.85 | 39046.44 | 47470.22 | 36457.51 | 40253.02 | 39151.3 | 34274.9 | 32454.02 | 25671.79 | 38774.29 | 45942.72 | 463053.46
1991-92 | 41113.47 | 50860.74 | 47208.14 | 49653.69 | 37847.85 | 37085.37 | 36864.35 | 30817.13 | 39190.54 | 33672.49 | 37280.92 | 32377.89 | 473972.58
1992-93 | 38314.85 | 42152.25 | 37079.75 | 46777.86 | 33218.57 | 40339.61 | 37360.15 | 39558.76 | 46266.57 | 38935.94 | 43266.57 | 36921.27 | 480192.15
1993-94 | 40091.94 | 40591.98 | 44375.95 | 43186.49 | 44626.02 | 41549.88 | 40723.46 | 37921.42 | 44894.64 | 36792.89 | 37620.55 | 35346.3 | 487721.52
1994-95 | 45600.2 | 44893.52 | 52046.86 | 52102.41 | 31287.66 | 42689.29 | 43780.36 | 39800.33 | 40413.64 | 39014.34 | 41888.24 | 34366.22 | 507883.07
1995-96 | 46925.95 | 51452.69 | 46912.74 | 43310.12 | 41541.3 | 41915.28 | 43312.45 | 43312.45 | 41359.76 | 43473.7 | 43714.81 | 44719.41 | 531950.66
1996-97 ($559,179) | 36089.46 | 55056.45 | 46912.74 | 56136.57 | 44123.69 | 45668.97 | 44214.67 | 45688.5 | 47543.95 | 44095.82 | 46660.08 | 46988.51 | 559179.41
1997-98 ($613,894) | 51716.17 | 50880.21 | 52281.52 | 64303.48 | 56190.32 | 49899.49 | 50752.79 | 42517.47 | 46017.2 | 48439.02 | 48518 | 52378.32 | 613893.99
1998-99 ($626,968) | 56859.53 | 54769.44 | 61577.19 | 61033.56 | 52785.32 | 46722.9 | 51000.75 | 45236.65 | 49097.71 | 47346.81 | 53244.68 | 47022.4 | 626696.94
1999-00 ($621,699) | 51795.48 | 60748.07 | 59773.29 | 64595.98 | 52768.07 | 51195.01 | 51791.91 | 46138.66 | 47863.36 | 45512.26 | 47971.26 | 41545.57 | 621698.92
2000-01 ($567,550) | 50437.32 | 58385.34 | 75659.32 | 44676.62 | 40321.38 | 39542.88 | 48231.54 | 35124.09 | 50692.36 | 27815.23 | 48915.4 | 47748.59 | 567550.07
2001-02 ($640,022) | 60568.28 | 80559.47 | 58604.17 | 44218.28 | 60031.62 | 50221.63 | 41399.07 | 60250.73 | 40347.55 | 48772.09 | 53994.66 | 41054.88 | 640022.43
2002-03 ($637,914) | 59752.38 | 67141.22 | 57980.87 | 65093.01 | 42350.29 | 54781.48 | 40805.91 | 49771.51 | 51971.35 | 45086.04 | 51176.88 | 52002.85 | 637913.79
2003-04 ($639,256) | 55074.63 | 58882.69 | 68025.47 | 59587.77 | 60317.21 | 45625.39 | 52572.23 | 47503.98 | 49614.92 | 39192.97 | 56545.28 | 46313.9 | 639256.44
2004-05 ($677,250) | 54260.62 | 63469.84 | 56512.7 | 68456.06 | 53441.57 | 53882.23 | 50785.28 | 50212.8 | 58761.35 | 57560.21 | 55329.03 | 54578.99 | 677250.68
2005-06 ($807,129) | 68546.08 | 76184.17 | 79427.8 | 78117.58 | 61548.14 | 57570.61 | 68579.44 | 63251.23 | 75515.97 | 65617.58 | 60893.45 | 51877.3 | 807129.35
2006-07 ($770,180) | 63733.17 | 88526.74 | 82293.42 | 85211.58 | 72564.82 | 64331.44 | 64468.21 | 61057.55 | 65068.1 | 64259.32 | 67892.13 | 57182.14 | 836588.62
2007-08 ($796,219) | 71047.17 | 88678.11 | 78241.95 | 72049.35 | 54836.99 | 59534.08 | 69111 | 60478.93 | 65735.48 | 60521.62 | 59102.9 | 56881.26 | 796218.84
2008-09 ($947,030) | 68156.67 | 105646.86 | 101187.56 | 98557.74 | 67070 | 75397.7 | 75465.64 | 70186.36 | 78862.78 | 70351.45 | 69667.75 | 66479.77 | 947030.28
2009-10 ($853,399)* | 59417.35 | 97080 | 77542 | 87056 | 78767 | 75774 | 82198 | 74977 | 75174 | 70736 | 17706 | 56972 | 853399.35
2010-11 ($908,134) | 77516.94 | 92420.2 | 84141.52 | 83194.55 | 72091.97 | 70693.15 | 77058 | 71415 | 69530 | 68396 | 70953 | 70724 | 908134.33
2011-12 ($903,976) | 74721 | 95764 | 84510 | 89771 | 76422 | 62656 | 77041 | 69266 | 71502 | 68952 | 69512 | 63859 | 903976
2012-13 ($979,799) | 81110 | 102382 | 80428 | 91329 | 78146 | 75530 | 77403 | 73147 | 83128 | 75667 | 79992 | 81537 | 979799
Previous five years (average) | 72184.392 | 98658.612 | 85561.816 | 89981.658 | 74499.394 | 72010.17 | 77833.128 | 71798.272 | 75639.356 | 70820.49 | 61566.15 | 67914.354 | 918467.792
* - Credits totalling $53,244 were taken in the last three months of FY due to Xcel overcharging for taxes

## KW Demand
ELECTRICITY DEMAND KW
| JUN | JULY | AUG | SEPT | OCT | NOV | DEC | JAN | FEB | MAR | APR | MAY | TOTAL
1991-92 | 1940 | 1940 | 2040 | 2112 | 1800 | 1704 | 1704 | 1704 | 1656 | 1704 | 1704 | 2112 | 22120
1992-93 | 1968 | 1920 | 1968 | 2112 | 2040 | 1824 | 1800 | 1704 | 1776 | 1752 | 1776 | 1992 | 22632
1993-94 | 1968 | 1944 | 2112 | 1920 | 1920 | 1752 | 1752 | 1752 | 1872 | 1776 | 1776 | 1944 | 22488
1995-96 | 1992 | 2088 | 2088 | 1992 | 1608 | 1776 | 1776 | 1776 | 1776 | 1920 | 1920 | 1992 | 22704
1996-97 | 2064 | 2136 | 2184 | 2280 | 1968 | 2112 | 1968 | 1968 | 1896 | 1920 | 2256 | 1896 | 24648
1997-98 | 2232 | 2280 | 2040 | 2592 | 2592 | 2256 | 2040 | 1872 | 1992 | 2016 | 2208 | 2328 | 26448
1998-99 | 2376 | 2208 | 2280 | 2448 | 2208 | 2208 | 1920 | 1824 | 2040 | 2016 | 2256 | 2328 | 26112
1999-2000
2000-2001
2001-2002 | 2230 | 2230 | 2230 | 2230 | 2001 | 2136 | 2105 | 2093 | 2133 | 2081 | 2500 | 1970 | 25939
2002-2003 | 2711 | 2653 | 2330 | 2778 | 2477 | 2136 | 2208 | 2112 | 2196 | 2134 | 2712 | 2292 | 28739
2003-2004 | 2429 | 2526 | 2626 | 2759 | 2833 | 2208 | 2112 | 2136 | 2127 | 2098 | 2237 | 2189 | 28280
2004-2005 | 2228 | 2298 | 2077 | 2494 | 2624 | 2133 | 2092 | 1937 | 2349 | 2161 | 2500 | 2340 | 27233
2005-2006 | 2500 | 2500 | 2500 | 2393 | 2439 | 2163 | 2141 | 2009 | 2103 | 2088 | 2339 | 1992 | 27167
2006-2007 | 2280 | 3024 | 2568 | 2232 | 2520 | 2400 | 2016 | 1752 | 1920 | 1800 | 1752 | 1751 | 26015
2007-2008 | 1941 | 2308 | 2352 | 1776 | 1571 | 1939 | 1809 | 1633 | 1739 | 1851 | 1823 | 1764 | 22506
2008-2009 | 1980 | 2681 | 2717 | 2587 | 2247 | 2163 | 1890 | 1953 | 1974 | 1911 | 1981 | 2151 | 26235
2009-2010-Chiller | 0 | 942.94 | 427 | 501 | 367 | 126 | 112 | 131 | 116 | 135 | 163 | 478 | 3498.94
2009-2010-Main | 1711 | 1627 | 1617 | 1855 | 2058 | 1974 | 1932 | 1911 | 1953 | 1890 | 1995 | 1906 | 22429
2010-2011-Chiller | 842 | 1052 | 963 | 949 | 490 | 98 | 86 | 59 | 64 | 62 | 105 | 722 | 5492
2010-2011-Main | 1626 | 1654 | 1572 | 1869 | 1974 | 2058 | 1995 | 1869 | 1932 | 1806 | 1764 | 1701 | 21820
2011-2012-Chiller | 1059 | 1713 | 1094 | 1109 | 857 | 290 | 204 | 176 | 98 | 116 | 89 | 857 | 7662
2011-2012-Main | 1245 | 1393 | 1231 | 1575 | 1764 | 1827 | 1827 | 1785 | 1848 | 1848 | 1827 | 1688 | 19858
2012-2013-Chiller | 1054 | 1136 | 1091 | 648 | 535 | 76 | 68 | 80 | 60 | 75 | 66 | 488 | 5377
2012-2013-Main | 1578 | 1722 | 1497 | 1743 | 1911 | 1890 | 1848 | 1764 | 1932 | 1827 | 1911 | 1890 | 21513
PREV. 4 YRS. AVG. MAIN | 1540 | 1599 | 1479.25 | 1760.5 | 1926.75 | 1937.25 | 1900.5 | 1832.25 | 1916.25 | 1842.75 | 1874.25 | 1796.25 | 21405
PREV. 4 YRS. AVG. CHILLER | 738.75 | 1210.985 | 893.75 | 801.75 | 562.25 | 147.5 | 117.5 | 111.5 | 84.5 | 97 | 105.75 | 636.25 | 5507.485

## KW Demand Cost
ELECTRICITY DEMAND KW COST - MAIN
| JUN | JULY | AUG | SEPT | OCT | NOV | DEC | JAN | FEB | MAR | APR | MAY | TOTAL
1992-93 | 15192.96 | 14822.4 | 15192.96 | 11302.08 | 10423.68 | 9959.04 | 9828 | 9303.84 | 9696.96 | 9565.92 | 9696.96 | 10876.32 | 135861.12
1993-94 | 15195.96 | 14822.4 | 16304.34 | 12968.46 | 12968.46 | 9565.92 | 9565.92 | 9565.92 | 10221.12 | 9696.96 | 10052.16 | 11003.04 | 141930.66
1994-95 | 16553.52 | 19086.41 | 17929.65 | 14404.55 | 10019.17 | 11003 | 11369.81 | 11369.81 | 12669.7 | 11229.44 | 11740.28 | 13838.76 | 161214.1
1995-96 | 16553 | 19086 | 17929 | 14404 | 10019 | 11003 | 11369 | 11369 | 12669 | 11229 | 11740 | 13868 | 161238
1996-97 | 13721 | 17158 | 18149 | 18947 | 11138 | 11954 | 11510 | 11510 | 11320 | 10867 | 12769 | 10731 | 159774
1997-98 | 18547 | 18947 | 16952 | 21539 | 14670 | 12769 | 11546 | 10595 | 11275 | 11411 | 12497 | 13176 | 173924
1998-99 | 19744.56 | 18348.48 | 18946.8 | 20342.88 | 12497.82 | 12497.28 | 10867.2 | 10323.84 | 11546 | 11411 | 12769 | 13176 | 172470.86
1999-2000
2000-2001 | 17550.72 | 18531.3 | 23593.75 | 14963.35 | 10595.52 | 10595.52 | 10052.15 | 10595.52 | 10609.1 | 7607.04 | 12361.44 | 8422.08 | 155477.49
2001-2002 | 19013.9 | 20473.14 | 19784.5 | 14532.82 | 13255.72 | 12089.76 | 11914.3 | 15400.28 | 9658.22 | 11778.46 | 14080.8 | 11150.2 | 173132.1
2002-2003 | 19993.39 | 21307.44 | 18878.6 | 21742.44 | 12443.62 | 12089.76 | 12497.28 | 11953.91 | 12429.36 | 14561.1 | 13454.6 | 12525.42 | 183876.92
2003-2004 | 18505.86 | 19436.31 | 21007.56 | 20888.84 | 14703.56 | 12497.28 | 11953.91 | 12089.76 | 12038.82 | 9142.26 | 14349.6 | 12389.74 | 179003.5
2004-2005 | 18514.68 | 19096.38 | 17259.87 | 17486.83 | 14150 | 12072.78 | 11840.72 | 10963.42 | 15124.45 | 13913.97 | 16096.69 | 15066.5 | 181586.29
2005-2006 | 19450 | 20775 | 20775 | 19885.83 | 15420.58 | 12242.58 | 12118.06 | 11370.94 | 11902.98 | 11818.08 | 13238.74 | 11274.72 | 180272.51
2006-2007 | 17134 | 25129.44 | 21340.08 | 18547.92 | 16335.68 | 13584 | 11410.56 | 9916.32 | 11231.34 | 10638 | 10354.32 | 10348.41 | 175970.07
2007-2008 | 16225.47 | 21349 | 21756 | 16428 | 10008.35 | 11459.49 | 10691.19 | 9651.03 | 10277.49 | 10939.41 | 10773.93 | 13250.58 | 162809.94
2008-2009 | 18315 | 24799.25 | 25132.25 | 23929.75 | 14083.88 | 12783.33 | 11169.9 | 11542.23 | 11666.34 | 11294.01 | 11707.71 | 12712.41 | 189136.06
2009-2010 | 15261.48 | 23771.75 | 19711.5 | 23462.5 | 15633.83 | 13442.94 | 13156.92 | 13013.91 | 13299.93 | 12870.9 | 12291.95 | 11779.08 | 187696.69
2010-2011 | 14685.4 | 15845.32 | 15059.76 | 17905.02 | 13317.92 | 12718.44 | 12329.1 | 11550.42 | 11939.76 | 11161.08 | 10902 | 10512.18 | 157926.4
2011-2012 | 11636 | 13345 | 11793 | 15089 | 11729 | 11290.86 | 11291 | 11031 | 11421 | 11421 | 11290.86 | 10432 | 141769.72
2012-2013 | 14402 | 16497 | 14341 | 19102 | 15566 | 14156.1 | 13842 | 13212 | 14471 | 13684 | 14313 | 14156 | 177742.1
PREV. 3 YEARS AVERAGE | 13574.4667 | 15229.1067 | 13731.2533 | 17365.34 | 13537.64 | 12721.8 | 12487.3667 | 11931.14 | 12610.5867 | 12088.6933 | 12168.62 | 11700.06 | 159146.0733
ELECTRICITY DEMAND KW COST - CHILLER
| JUN | JULY | AUG | SEPT | OCT | NOV | DEC | JAN | FEB | MAR | APR | MAY | TOTAL
2009-2010 | 0 | 8722 | 3950 | 4634.25 | 702.35 | 744.66 | 661.92 | 774.21 | 685.56 | 797.85 | 1000.24 | 2954.04 | 25627.08
2010-2011 | 7529.57 | 10078.16 | 9225.54 | 9091.42 | 3305.88 | 605.64 | 531.48 | 364.62 | 395.52 | 383.16 | 649 | 4461.96 | 46621.95
2011-2012 | 9897 | 16411 | 10481 | 10624 | 5698 | 1792.2 | 1261 | 10888 | 606 | 717 | 550.02 | 5296 | 74221.22
2012-2013 | 9620 | 10883 | 709 | 7102 | 4445 | 569.24 | 509 | 599 | 449 | 562 | 494 | 3655 | 39596.24
PREV. 3 YEARS AVERAGE | 9015.5233 | 12457.3867 | 6805.18 | 8939.14 | 4482.96 | 989.0267 | 767.16 | 3950.54 | 483.5067 | 554.0533 | 564.34 | 4470.9867 | 53479.8033

## ELECOMs
1996-97 ($559,179) | 36089.46 | 55056.45 | 46912.74 | 56136.57 | 44123.69 | 45668.97 | 44214.67 | 45688.5 | 47543.95 | 44095.82 | 46660.08 | 46988.51 | 559179.41
1997-98 ($613,894) | 51716.17 | 50880.21 | 52281.52 | 64303.48 | 56109.32 | 49899.49 | 50752.79 | 42517.47 | 46017.2 | 48439.02 | 48518 | 52378.32 | 613812.99
1998-99 ($626,696) | 56859.53 | 54769.44 | 61577.19 | 61033.56 | 52785.32 | 46722.9 | 51000.75 | 45236.65 | 49097.71 | 47346.81 | 53244.68 | 52378.32 | 632052.86
1999-00 ($621,699) | 51795.48 | 60748.07 | 59773.29 | 64595.98 | 52768.07 | 51195.01 | 51791.91 | 46138.66 | 47863.36 | 45512.26 | 47971.26 | 41545.57 | 621698.92
1996-97 (11,988,879 kwh) | 727680 | 1204800 | 691200 | 1070400 | 960000 | 998400 | 1039898 | 1074562 | 1135139 | 1036800 | 972000 | 1078000 | 11988879
1997-98 (12,782,400 kwh) | 940800 | 979200 | 1008000 | 1135200 | 1144800 | 1096800 | 1195200 | 936000 | 1034400 | 1161600 | 1039200 | 1111200 | 12782400
1998-99 (12,972,000 kwh) | 1012800 | 1022400 | 1212000 | 1128000 | 1128000 | 945600 | 1195200 | 1056000 | 1101600 | 1039200 | 1130400 | 1000800 | 12972000
1999-00 (12,117,600 kwh) | 974400 | 1123200 | 1125600 | 1096800 | 1020000 | 1099200 | 849600 | 1020000 | 1039200 | 936000 | 878400 | 955200 | 12117600
2000-01 (11,611,968 kwh) | 960000 | 1058400 | 1468800 | 891072 | 909792 | 876096 | 1096992 | 662688 | 1029600 | 692640 | 1048320 | 917568 | 11611968
| JUN | JUL | AUG | SEP | OCT | NOV | DEC | JAN | FEB | MAR | APR | MAY
2000-01 ($567,550) | 50437.32 | 58385.34 | 75659.32 | 44676.62 | 40321.38 | 39542.88 | 48231.54 | 35124.09 | 50692.36 | 27815.23 | 48915.4 | 47748.59 | 567550.07
2001-02 ($642,002) | 60568.28 | 80559.47 | 58604.17 | 44218.28 | 60031.62 | 50221.63 | 41399.07 | 60250.73 | 40347.55 | 48772.09 | 53994.66 | 41054.88 | 640022.43
2002-03 ($637,914) | 59752.38 | 67141.22 | 57980.87 | 65093.01 | 42350.29 | 54781.48 | 40805.91 | 49771.51 | 51971.35 | 45086.04 | 51176.88 | 52002.85 | 637913.79
2003-04 ($639,256) | 55074.63 | 58882.69 | 68025.47 | 59587.77 | 60317.21 | 45625.39 | 52572.23 | 47503.98 | 49614.92 | 39192.97 | 56545.28 | 46313.9 | 639256.44
2004-05 ($677,251) | 54260.62 | 63469.84 | 56512.7 | 68456.06 | 53441.57 | 53882.23 | 50785.28 | 50212.8 | 58761.35 | 57560.21 | 55329.03 | 54578.99 | 677250.68
2005-06 ($807,129) | 68546.08 | 76184.17 | 79427.8 | 78117.58 | 61548.14 | 57570.61 | 68579.44 | 63251.23 | 75515.97 | 65617.58 | 60893.45 | 51877.3 | 807129.35
2006-07 ($836,589) | 63733.17 | 88526.74 | 82293.42 | 85211.58 | 72564.82 | 64331.44 | 64468.21 | 61057.55 | 65068.1 | 64259.32 | 67892.13 | 57182.14 | 836588.62
2007-08 ($796,219) | 71047.17 | 88678.11 | 78241.95 | 72049.35 | 54836.99 | 59534.08 | 69111 | 60478.93 | 65735.48 | 60521.62 | 59102.9 | 56881.26 | 796218.84
2008-09 ($947,030) | 68156.67 | 105646.86 | 101187.56 | 98557.74 | 67070 | 75397.7 | 75465.64 | 70186.36 | 78862.78 | 70351.45 | 69667.75 | 66479.77 | 947030.28
2009-10 ($853,399) | 59417.35 | 97080 | 77542 | 87056 | 78767 | 75774 | 82198 | 74977 | 75174 | 70736 | 17706 | 56972 | 853399.35
2010-11 ($908,135) | 77517 | 92420 | 84142 | 83195 | 72092 | 70693 | 77058 | 71415 | 69530 | 68396 | 70953 | 70724 | 908135
2011-12 ($903,976) | 74721 | 95764 | 84510 | 89771 | 76422 | 62656 | 77041 | 69266 | 71502 | 68952 | 69512 | 63859 | 903976
2012-13 ($979,799) | 81110 | 102382 | 80428 | 91329 | 78146 | 75530 | 77403 | 73147 | 83128 | 75667 | 79992 | 81537 | 979799
2001-02 (12,739,200kWh) | 1000800 | 1365600 | 924000 | 837600 | 1231200 | 1116000 | 856800 | 1293600 | 926400 | 1094400 | 1243200 | 849600 | 12739200
2002-03 (13,257,600 kWh) | 1056000 | 1262400 | 1020000 | 1329600 | 998400 | 1291200 | 854400 | 1128000 | 1240800 | 976800 | 1101600 | 998400 | 13257600
2003-04 (12,969,600kWh) | 967200 | 1039200 | 1240800 | 1159200 | 1257600 | 1015200 | 1180800 | 1041600 | 1060800 | 844800 | 1274400 | 888000 | 12969600
2004-05 (12,944,171kWh) | 899585 | 1105860 | 977142 | 1265510 | 1079949 | 1045310 | 1015844 | 1087376 | 1196023 | 1237149 | 1045415 | 989008 | 12944171
2005-06 (13,058,757kWh) | 1029339 | 1209515 | 1077824 | 1224364 | 1065547 | 1007698 | 1236344 | 1033577 | 1140243 | 1071488 | 1012501 | 950317 | 13058757
2006-07 (12,399,200kWh) | 1005600 | 1171200 | 1056000 | 1118400 | 1036800 | 1075200 | 1075200 | 938400 | 1048800 | 1070400 | 959000 | 844200 | 12399200
2007-08 (10,787,257kWh) | 872200 | 982800 | 890400 | 1080800 | 905800 | 910000 | 996800 | 814800 | 950600 | 848400 | 889000 | 645657 | 10787257
2008-09 (12,337,600kWh) | 737100 | 1125600 | 1106700 | 1283100 | 942900 | 1033200 | 1106700 | 1001700 | 1155000 | 926200 | 1008000 | 911400 | 12337600
2009-10 (11,670,400kWh) | 701400 | 1087100 | 866600 | 1066100 | 996800 | 980000 | 1106000 | 1047200 | 1045800 | 980000 | 945000 | 848400 | 11670400
2010-11 (11,887,400kWh) | 945000 | 1044400 | 983500 | 992600 | 998200 | 1003100 | 1118600 | 1021300 | 1008000 | 968800 | 947800 | 856100 | 11887400
2011-12 (11,454,100kWh) | 812000 | 1013600 | 978600 | 975100 | 963200 | 918400 | 1080100 | 929600 | 1026200 | 931000 | 1026200 | 800100 | 11454100
2012-13 (11,916,100kWh) | 912800 | 1193500 | 866600 | 1045800 | 947800 | 1035300 | 1059100 | 953400 | 1057700 | 971600 | 1005200 | 867300 | 11916100

## Fuel Costs
COST OF GAS AND OIL
| JUN | JUL | AUG | SEP | OCT | NOV | DEC | JAN | FEB | MAR | APR | MAY | TOTAL
1989-90 | 0 | 0 | 1671.63 | 7253.34 | 17630.36 | 32716.96 | 42366.81 | 44027.01 | 34538.38 | 27473.6 | 16807.89 | 5040.52 | 229526.5
1990-91 | 0 | 0 | 291.5 | 3837.1 | 16924.99 | 31880.28 | 46660.15 | 52425.97 | 38789.76 | 38003.13 | 15708.77 | 3301.84 | 247823.49
1991-92 | 290.13 | 290.13 | 290.13 | 2866.55 | 13910.59 | 24580.49 | 26474.94 | 29092.45 | 23169.06 | 19766.86 | 14441.43 | 4598 | 159770.76
1992-93 | 288.75 | 288.75 | 1392.574 | 8056.64 | 24858.19 | 33944.9 | 36597.08 | 37666.34 | 40480.24 | 39229.84 | 28818.27 | 7191.31 | 258812.884
1993-94 | 293.25 | 293.25 | 697.82 | 6527.91 | 19150.61 | 29301.55 | 31912.22 | 40397.79 | 35193.32 | 27280 | 16273.2 | 4786.13 | 212107.05
1994-95 | 288.75 | 288.75 | 1151.1 | 2292.35 | 10657.36 | 21758.26 | 30701.63 | 27292.94 | 19216.89 | 20358.27 | 16902.56 | 4753.26 | 155662.12
1995-96 | 288.75 | 288.75 | 288.75 | 4332.94 | 14332.72 | 26743.22 | 26190.43 | 32872.05 | 38188.42 | 34119.99 | 26100.05 | 8030.53 | 211776.6
1996-97 | 288.75 | 288.75 | 288.75 | 288.75 | 18560.04 | 45036.62 | 56549.53 | 76119.06 | 41494.11 | 25949.29 | 16174.57 | 12108.04 | 293146.26
1997-98 | 288.75 | 288.75 | 288.75 | 288.75 | 20555.82 | 45722.06 | 38797.91 | 35106.45 | 26520.32 | 31884.38 | 16972 | 4120.46 | 220834.4
1998-99 | 288.75 | 288.76 | 288.75 | 2018.24 | 18469.39 | 26298.58 | 37553.09 | 41044.13 | 27808.52 | 24531.35 | 15853.85 | 5009.36 | 199452.77
1999-00 ($221,413) | 288.75 | 288.755 | 288.75 | 983.5 | 20197.96 | 28859.89 | 35145.45 | 42257.41 | 36007.86 | 28525.76 | 24229.36 | 4339.67 | 221413.115
2000-01 ($506,962) | 288.75 | 288.75 | 308.75 | 2596.64 | 35860.04 | 59465.72 | 96326.24 | 93743.34 | 88344.05 | 70520.56 | 45814.83 | 13404.37 | 506962.04
2001-02 ($326,532) | 288.75 | 288.755 | 288.75 | 3851.42 | 18462.32 | 35100.82 | 54182.28 | 59123.34 | 51217.99 | 52101.56 | 35390.55 | 16235.31 | 326531.845
2002-03 ($432,450) | 309.25 | 309.25 | 309.25 | 4947.46 | 39439.27 | 56828.56 | 52623.49 | 67888.93 | 71725.89 | 70425.72 | 51597.23 | 16045.48 | 432449.78
2003-04 ($423,755) | 309.25 | 314.99 | 309.25 | 9400.35 | 34165.61 | 62379.69 | 58806.6 | 78433.71 | 73578.58 | 54570.84 | 37895.53 | 13590.76 | 423755.16
2004-05 ($461,911) | 388.45 | 309.75 | 309.75 | 331.77 | 34964.75 | 47832.31 | 83109.12 | 95724.32 | 64052.589 | 76128.133 | 47603.27 | 11156.42 | 461910.632
2005-06 ($715,476) | 324.12 | 324.12 | 324.12 | 14185.86 | 110146.71 | 148118.98 | 129734.79 | 89203.79 | 96262.032 | 86711.97 | 30262.51 | 9876.74 | 715475.742
2006-07 ($421,140) | 499.54 | 309.75 | 309.75 | 18234.87 | 39441.44 | 71395.9 | 66739.42 | 73583.12 | 77936.65 | 21428.1 | 44747.94 | 6513.7 | 421140.18
2007-08 ($785,944) | 306.21 | 306.21 | 306.21 | 306.21 | 36287.47 | 92517.5 | 133687.67 | 149480.89 | 151876.01 | 122751.25 | 77871.16 | 21216.32 | 786913.11
2008-09 ($514,774) | 311.17 | 311.17 | 311.17 | 4061.93 | 40229.89 | 82558.79 | 98179.09 | 103166.7 | 72481.18 | 62952.84 | 40032.85 | 10177.04 | 514773.82
2009-10 ($461,433) | 311.17 | 311.17 | 311.17 | 1220.71 | 39543.95 | 46604.18 | 90230.77 | 120373.71 | 79086.91 | 47115.83 | 23692.3 | 12631.13 | 461433
2010-11 ($494,775) | 332.59 | 338.12 | 332.59 | 337 | 21530 | 57297 | 100001 | 90111 | 76186 | 69476 | 68991 | 9842.22 | 494774.52
2011-12 ($316,037) | 311.17 | 311.17 | 311.17 | 921 | 24175 | 52924 | 66790 | 60419 | 56345 | 28973 | 20384 | 4172 | 316036.51
2012-13 ($393,809) | 311.17 | 311.17 | 311.17 | 2573 | 28322 | 46005 | 63048 | 63343 | 60296 | 71437 | 43192 | 14660 | 393809.51
PREV. 5 YR. AVG. | 315.454 | 316.56 | 315.454 | 1822.728 | 30760.168 | 57077.794 | 83649.772 | 87482.682 | 68879.018 | 55990.934 | 39258.43 | 10296.478 | 436165.472

## BTUCOMS
YEAR | JUN | JUL | AUG | SEP | OCT | NOV | DEC | JAN | FEB | MAR | APR | MAY | TOTAL
BTU CONSUMPTION (X100k) | [12 empty] | (x1,000,000)
1990-91 | 614 | 1002 | 0 | 1928 | 7874 | 11939 | 17525 | 19717 | 14558 | 14259 | 7891 | 1431 | 98738
1991-92 | 0 | 0 | 0 | 1202 | 7265 | 17945 | 14660 | 14841 | 13590 | 11751 | 8715 | 2299 | 92268
1992-93 | 0 | 0 | 409 | 2964 | 7393 | 12550 | 15372 | 16846 | 15458 | 9169 | 13671 | 2144 | 95976
1993-94 | 0 | 0 | 159 | 2305 | 7588 | 11335 | 12733 | 16627 | 14967 | 10545 | 6351 | 1961 | 84571
1994-95 | 0 | 0 | 275 | 1031 | 5650 | 9983 | 13049 | 14129 | 11594 | 10552 | 8831 | 2351 | 77445
1995-96 | 0 | 0 | 224 | 2249 | 7187 | 12545 | 13706 | 16049 | 14292 | 13114 | 9072 | 3371 | 91809
1996-97 | 0 | 0 | 0 | 0 | 8136 | 15131 | 17211 | 18573 | 14593 | 13176 | 7953 | 5218 | 99991
1997-98 | 0 | 0 | 0 | 0 | 6058 | 13793 | 14768 | 15811 | 11057 | 12651 | 6650 | 1626 | 82414
1998-99 | 0 | 0 | 0 | 901 | 7039 | 11084 | 15072 | 18574 | 12758 | 11701 | 7595 | 1964 | 86688
TOTAL | 68.2222 | 111.3333 | 118.5556 | 1397.7778 | 7132.2222 | 12922.7778 | 14899.5556 | 16796.3333 | 13651.8889 | 11879.7778 | 8525.4444 | 2485 | 89988.8889
COST OF GAS AND OIL
YEAR | JUN | JUL | AUG | SEP | OCT | NOV | DEC | JAN | FEB | MAR | APR | MAY | TOTAL
1989-90 | 0 | 0 | 1671.63 | 7253.34 | 17630.36 | 32716.96 | 42366.81 | 44027.01 | 34538.38 | 27473.6 | 16807.89 | 5040.52 | 229526.5
1990-91 | 0 | 0 | 291.5 | 3837.1 | 16924.99 | 31880.28 | 46660.15 | 52425.97 | 38789.76 | 38003.13 | 15708.77 | 3301.84 | 247823.49
1991-92 | 290.13 | 290.13 | 290.13 | 2866.55 | 13910.59 | 24580.49 | 26474.94 | 29092.45 | 23169.06 | 19766.86 | 14441.43 | 4598 | 159770.76
1992-93 | 288.75 | 288.75 | 1392.574 | 8056.64 | 24858.19 | 33944.9 | 36597.08 | 37666.34 | 40480.24 | 39229.84 | 28818.27 | 7191.31 | 258812.884
1993-94 | 293.25 | 293.25 | 697.82 | 6527.91 | 19150.61 | 29301.55 | 31912.22 | 40397.79 | 35193.32 | 27280 | 16273.2 | 4786.13 | 212107.05
1994-95 | 288.75 | 288.75 | 1151.1 | 2292.35 | 10657.36 | 21758.26 | 30701.63 | 27292.94 | 19216.89 | 20358.27 | 16902.56 | 4753.26 | 155662.12
1995-96 | 288.75 | 288.75 | 288.75 | 4332.94 | 14332.72 | 26743.22 | 26190.43 | 32872.05 | 38188.42 | 34119.99 | 26100.05 | 8030.53 | 211776.6
1996-97 | 288.75 | 288.75 | 288.75 | 288.75 | 18560.04 | 45036.62 | 56549.53 | 76119.06 | 41494.11 | 25949.29 | 16174.57 | 12108.04 | 293146.26
1997-98 | 288.75 | 288.75 | 288.75 | 288.75 | 20555.82 | 45722.06 | 38797.91 | 35106.45 | 26520.32 | 31884.38 | 16972 | 4120.46 | 220834.4
1998-99 | 288.75 | 288.76 | 288.75 | 2018.24 | 18469.39 | 26298.58 | 37553.09 | 41044.13 | 27808.52 | 24531.35 | 15853.85 | 5009.36 | 199452.77
TOTAL | 174.426 | 174.426 | 868.7308 | 5708.308 | 18494.948 | 30484.836 | 36802.24 | 40721.912 | 34434.152 | 30350.686 | 18409.912 | 4983.56 | 127424.15
1996-97 (99.99 BIL Btus) | 0 | 0 | 0 | 0 | 8136 | 15131 | 17211 | 18573 | 14593 | 13176 | 7953 | 5218
| JUN | JUL | AUG | SEP | OCT | NOV | DEC | JAN | FEB | MAR | APR | MAY
1997-98 (82.41 BIL Btus) | 0 | 0 | 0 | 0 | 6058 | 13793 | 14768 | 15811 | 11057 | 12651 | 6650 | 1626
1998-99 (86.67 BIL Btus) | 0 | 0 | 0 | 901400 | 7039200 | 11084400 | 15061736 | 18574200 | 12758000 | 11700800 | 7595200 | 1964300 | 86679236
1999-00 (76.96 BIL Btus) | 0 | 0 | 0 | 220900 | 6917400 | 8867600 | 13369310 | 16118600 | 12526905 | 9955900 | 7720300 | 1262900 | 76959815
2000-01 (94.7 BIL Btus) | 0 | 0 | 0 | 468000 | 6354800 | 12605900 | 19682500 | 15766350 | 15803900 | 13307450 | 8176900 | 2535700 | 94701500
2001-02 (84.2 BIL Btus) | 0 | 0 | 0 | 1235500 | 7924900 | 8564900 | 13970210 | 14639200 | 11545805 | 13693100 | 8430600 | 4174700 | 84178915
1996-97 ($293,146) | 288.75 | 288.75 | 288.75 | 288.75 | 18560.04 | 45036.62 | 56549.53 | 76119.06 | 41494.11 | 25949.29 | 16174.57 | 12108.04
1997-98 ($220,834) | 288.75 | 288.75 | 288.75 | 288.75 | 20555.82 | 45722.06 | 38797.91 | 35106.45 | 26520.32 | 31884.38 | 16972 | 4120.46
1998-99 ($197,453) | 288.75 | 288.76 | 288.75 | 2018.24 | 16469.39 | 26298.58 | 37553.09 | 41044.13 | 27808.52 | 24531.35 | 15853.85 | 5009.36 | 197452.77
1999-00 ($221,394) | 288.75 | 288.755 | 288.75 | 983.5 | 20197.96 | 28859.89 | 35145.45 | 42257.41 | 35988.96 | 28525.76 | 24229.36 | 4339.67 | 221394.215
2000-01 ($506,962) | 288.75 | 288.75 | 308.75 | 2596.64 | 35860.04 | 59465.72 | 96326.24 | 93743.34 | 88344.05 | 70520.56 | 45814.83 | 13404.37 | 506962.04
2001-02 ($319,000) | 288.75 | 288.755 | 288.75 | 3851.42 | 18462.32 | 35100.82 | 54767.46 | 59123.34 | 45623.64 | 52101.56 | 33517.37 | 16235.31 | 319649.495
| JUN | JUL | AUG | SEP | OCT | NOV | DEC | JAN | FEB | MAR | APR | MAY
2002-03 (91.3 BIL Btus) | 0 | 0 | 0 | 1319000 | 9450000 | 11736000 | 13188150 | 16308500 | 15462200 | 11278600 | 9711000 | 2881000 | 91334450
2003-04 (89.5 BIL Btus) | 0 | 1000 | 0 | 1741000 | 7002000 | 11820000 | 15031250 | 16840950 | 16018546 | 11792050 | 6984000 | 2270000 | 89500796
2004-05 (BIL Btus) | 12000 | 0 | 0 | 4000 | 6286000 | 8603800 | 16086050 | 13577100 | 0 | 0 | 0 | 0 | 44568950
| 3081.384 | 3773.1943 | 3334.0085 | 4321.9201 | 9970.786 | 12170.3977 | 19552.1097 | 20947.2769 | 16151.1805 | 17148.6024 | 9928.956 | 4838.4953
2002-03 (91.3 BIL Btus) | 0 | 0 | 0 | 1319000 | 9450000 | 11736000 | 13188150 | 16308500 | 15462200 | 11278600 | 9711000 | 2881000 | 91334450
| 0 | 1000 | 0 | 1741000 | 7002000 | 11820000 | 15031250 | 16840950 | 16018546 | 11792050 | 6984000 | 2270000 | 89500796
2003-04 (133 BIL Btus) | 3300000 | 3547000 | 4234000 | 5696000 | 11293000 | 15284000 | 19060000 | 20395000 | 19638000 | 14675000 | 11332000 | 5300000 | 133754000
2004-05 (125 BIL Btus) | 3081000 | 3773000 | 3334000 | 4322000 | 9971000 | 12170000 | 19552000 | 20947000 | 16151000 | 17149000 | 9929000 | 4838000 | 125217000
2005-06 (122 BIL Btus) | 3512000 | 4127000 | 3678000 | 5545000 | 12987000 | 16508000 | 16723000 | 14399000 | 17281000 | 15613000 | 7863000 | 4604000 | 122840000
2006-07 (115 BIL Btus) | 3434000 | 3996000 | 3603000 | 6305000 | 11013000 | 14237000 | 14449000 | 17688000 | 18567000 | 13035000 | 7273000 | 1604000 | 115204000
2007-08 (126 BIL Btus) | 2976000 | 3353000 | 3038000 | 3691000 | 8321000 | 14706000 | 19382000 | 21441000 | 18783000 | 15667000 | 10729000 | 3994000 | 126081000
2008-09 (85 BIL Btus) | 0 | 0 | 0 | 500000 | 6302000 | 11238000 | 14653650 | 17987700 | 14500150 | 10639000 | 6977000 | 2248000 | 85045500
2009-10 (78 BIL Btus) | 0 | 0 | 0 | 240000 | 8037000 | 8082000 | 15343850 | 16905550 | 13229000 | 8946000 | 4614000 | 2355000 | 77752400
2010-11 (81 BIL Btus) | 0 | 0 | 0 | 0 | 4343000 | 10898184 | 16562800 | 15380540 | 12788000 | 12000000 | 6904000 | 1932000 | 80808524
2011-12 ( 65 BIL Btus) | 0 | 0 | 0 | 119000 | 4726000 | 9983000 | 12738000 | 12291000 | 11934000 | 6124000 | 5408000 | 1268000 | 64591000
2012-13 ( 82 BIL Btus) | 0 | 0 | 0 | 622000 | 6898000 | 9891000 | 13579000 | 14777000 | 11905700 | 13268100 | 8624000 | 2745000 | 82309800
2002-03 ($432,450) | 309.25 | 309.25 | 309.25 | 4947.46 | 39439.27 | 56828.56 | 52623.49 | 67888.93 | 71725.89 | 70425.72 | 51597.23 | 16045.48 | 432449.78
2003-04 ($423,755) | 309.25 | 314.99 | 309.25 | 9400.35 | 34165.61 | 62379.69 | 58806.6 | 78433.71 | 73578.58 | 54570.84 | 37895.53 | 13590.76 | 423755.16
2004-05 ($461,911) | 388.45 | 309.75 | 309.75 | 331.77 | 34964.75 | 47832.31 | 83109.12 | 95724.32 | 64052.589 | 76128.133 | 47603.27 | 11156.42 | 461910.632
2005-06 ($715,476) | 324.12 | 324.12 | 324.12 | 14185.86 | 110146.71 | 148118.98 | 129734.79 | 89203.79 | 96262.032 | 86711.97 | 30262.51 | 9876.74 | 715475.742
2006-07 ($421,140) | 499.54 | 309.75 | 309.75 | 18234.87 | 39441.44 | 71395.9 | 66739.42 | 73583.12 | 77936.65 | 21428.1 | 44747.94 | 6513.7 | 421140.18
2007-08 ($785,994) | 306.21 | 306.21 | 306.21 | 306.21 | 36287.47 | 92517.5 | 133687.67 | 149480.89 | 151876.01 | 122751.25 | 77871.16 | 21216.32 | 786913.11
2008-09 ($514,774) | 311.17 | 311.17 | 311.17 | 4061.93 | 40229.89 | 82558.79 | 98179.09 | 103166.7 | 72481.18 | 62952.84 | 40032.85 | 10177.04 | 514773.82
2009-10 ($461,433) | 311.17 | 311.17 | 311.17 | 1220.71 | 39543.95 | 46604.18 | 90230.77 | 120373.71 | 79086.91 | 47115.83 | 23692.3 | 12631.13 | 461433
2010-11 ($494,775) | 332.59 | 338.12 | 332.59 | 337 | 21530 | 57297 | 100001 | 90111 | 76186 | 69476 | 68991 | 9842.22 | 494774.52
2011-12 ($316,037) | 311.17 | 311.17 | 311.17 | 921 | 24175 | 52924 | 66790 | 60419 | 56345 | 28973 | 20384 | 4172 | 316036.51
2012-13 ($393,810) | 311.17 | 311.17 | 311.17 | 2573 | 28322 | 46005 | 63048 | 63343 | 60296 | 71437 | 43192 | 14660 | 393809.51

## Heating Degree Days
| 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/00 | 00/01 | 01/02 | 02/03 | 03/04 | 04/05 | 05/06 | 06/07 | 07/08 | 08/09 | 09/10 | 10/11 | 11/12 | 12/13 | 18 Year Avg. |  | 10/11(7870) | 11/12(6302) | 12/13(7562) | 3 Year Avg.
JUN | 25 | 48 | 38 | 29 | 6 | 30 | 30 | 10 | 80 | 68 | 64 | 63 | 35 | 47 | 72 | 1 | 21 | 14 | 22 | 83 | 52 | 72 | 0 | 42.4444 | JUN | 52 | 72 | 0 | 41.3333
JUL | 3 | 46 | 12 | 0 | 0 | 2 | 0 | 21 | 0 | 0 | 14 | 9 | 0 | 2 | 12 | 2 | 0 | 0 | 0 | 40 | 6 | 2 | 2 | 6.2222 | JUL | 6 | 2 | 2 | 3.3333
AUG | 1 | 79 | 21 | 2 | 0 | 0 | 0 | 29 | 1 | 5 | 1 | 5 | 4 | 0 | 58 | 5 | 0 | 15 | 0 | 52 | 12 | 21 | 40 | 13.7778 | AUG | 12 | 21 | 40 | 24.3333
SEP | 86 | 339 | 114 | 226 | 88 | 188 | 123 | 97 | 67 | 177 | 152 | 183 | 132 | 188 | 74 | 69 | 220 | 121 | 121 | 86 | 189 | 196 | 107 | 138.3333 | SEP | 189 | 196 | 107 | 164
OCT | 425 | 668 | 493 | 462 | 336 | 485 | 438 | 465 | 465 | 489 | 364 | 513 | 725 | 448 | 484 | 431 | 598 | 369 | 469 | 671 | 393 | 392 | 515 | 484.1111 | OCT | 393 | 392 | 515 | 433.3333
NOV | 689 | 1300 | 927 | 910 | 743 | 1038 | 1100 | 1068 | 826 | 682 | 1006 | 301 | 977 | 969 | 809 | 824 | 844 | 916 | 904 | 677 | 900 | 797 | 811 | 858.2778 | NOV | 900 | 797 | 811 | 836
DEC | 1502 | 1441 | 1255 | 1155 | 1155 | 1346 | 1399 | 1160 | 1208 | 1189 | 1753 | 1148 | 1200 | 1227 | 1328 | 1390 | 1115 | 1472 | 1574 | 1455 | 1491 | 1151 | 1222 | 1323.7778 | DEC | 1491 | 1151 | 1222 | 1288
JAN | 1722 | 1405 | 1384 | 1692 | 1275 | 1596 | 1502 | 1338 | 1558 | 1498 | 1350 | 1234 | 1540 | 1663 | 1537 | 1082 | 1342 | 1576 | 1720 | 1588 | 1620 | 1281 | 1430 | 1469.7222 | JAN | 1620 | 1281 | 1430 | 1443.6667
FEB | 1254 | 1151 | 1466 | 1277 | 1090 | 1275 | 1063 | 918 | 1033 | 1068 | 1440 | 1014 | 1372 | 1226 | 1073 | 1226 | 1432 | 1413 | 1208 | 1256 | 1282 | 1074 | 1258 | 1201.7222 | FEB | 1282 | 1274 | 1258 | 1271.3333
MAR | 1146 | 922 | 948 | 796 | 739 | 1155 | 945 | 1030 | 921 | 754 | 1113 | 1239 | 1043 | 908 | 1019 | 966 | 837 | 1118 | 1004 | 736 | 1084 | 530 | 1161 | 975.7222 | MAR | 1084 | 530 | 1161 | 925
APR | 639 | 406 | 513 | 513 | 581 | 608 | 481 | 395 | 480 | 559 | 504 | 615 | 529 | 481 | 396 | 335 | 549 | 633 | 531 | 320 | 577 | 444 | 756 | 510.7222 | APR | 577 | 444 | 756 | 592.3333
MAY | 303 | 110 | 155 | 155 | 126 | 200 | 216 | 58 | 167 | 180 | 198 | 357 | 230 | 274 | 299 | 214 | 124 | 267 | 190 | 252 | 264 | 142 | 260 | 216.2222 | MAY | 264 | 142 | 260 | 222
0
| 7795 | 7915 | 7326 | 7217 | 6139 | 7923 | 7297 | 6589 | 6806 | 6669 | 7959 | 6681 | 7787 | 7433 | 7161 | 6545 | 7082 | 7914 | 7743 | 7216 | 7870 | 6102 | 7562 | 7241.0556 |  | 7870 | 6302 | 7562 | 7244.6667

## Cooling Degree Days
MACALESTER COLLEGE ACTUAL READINGS
COOLING DEGREE DAYS
|  | 89/90 | 90/91 | 91/92 | 92/93 | 93/94 | 94-95 | 95-96 | 96-97 | 97-98 (690) | 98-99 (750) | 99-00 (740) | 00/01 (612) | 01/02 ( 851) | 02/03 (859) | 03/04 (772) | 04/05 (485) | 05/06 (932) | 06/07 (909) | 07/08 (880) | 08/09 (716) | 09/10 (828) | 10/11 (935) | 11/12 (1177) | 12/13 (1242) | 3 YR AVE
| JUN | 101 | 285 | 116 | 182 | 111 | 287 | 306 | 233 | 192 | 113 | 135 | 106 | 175 | 199 | 123 | 86 | 225 | 175 | 214 | 118 | 140 | 152 | 178 | 277 | 202.3333
| JUL | 291 | 343 | 108 | 166 | 259 | 266 | 328 | 269 | 215 | 259 | 348 | 243 | 309 | 348 | 251 | 200 | 327 | 415 | 316 | 297 | 199 | 310 | 395 | 438 | 381
| AUG | 130 | 308 | 84 | 138 | 251 | 176 | 289 | 334 | 131 | 210 | 160 | 160 | 267 | 172 | 287 | 77 | 185 | 197 | 209 | 215 | 174 | 338 | 266 | 271 | 291.6667
| SEP | 12 | 166 | 7 | 32 | 9 | 101 | 72 | 104 | 34 | 125 | 54 | 49 | 44 | 115 | 92 | 110 | 89 | 32 | 107 | 56 | 153 | 41 | 101 | 148 | 96.6667
| OCT | 2 | 0 | 0 | 6 | 1 | 0 | 8 | 0 | 27 | 0 | 0 | 5 | 1 | 0 | 11 | 1 | 23 | 8 | 30 | 4 | 0 | 38 | 69 | 8 | 38.3333
| NOV | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.33333
| DEC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| JAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FEB | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MAR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 32 | 0 | 10.6667
| APR | 3 | 0 | 16 | 0 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 8 | 20 | 11 | 8 | 5 | 1 | 11 | 0 | 0 | 26 | 5 | 15 | 13 | 11
| MAY | 17 | 18 | 110 | 25 | 7 | 29 | 35 | 21 | 90 | 43 | 43 | 41 | 35 | 14 | 0 | 6 | 82 | 71 | 4 | 26 | 130 | 50 | 121 | 87 | 86
0
| TOTAL | 556 | 1121 | 441 | 549 | 645 | 859 | 1038 | 961 | 690 | 750 | 740 | 612 | 851 | 859 | 772 | 485 | 932 | 909 | 880 | 716 | 828 | 935 | 1177 | 1242 | 1118

## Past Data
| ACTUAL | BTUs | TOTAL | FUEL |  | TOTAL | ELECT | TOTAL | TOTAL | TOTAL | BTU | COST
YEAR | HEATING | CONSUMED | FUEL | COST | KWH | ELECTRIC | COST | SQUARE | BTU | BTU | CONSUMP | per
| DEGREE | x1,000,000 | COST | per | CONSUMED | COST | per | FEET | CONSUM | COST | per FOOT | 1 MIL
| DAYS |  |  | 100k BTU |  |  | KWH |  | (x1 MIL) |  |  | BTUs
84-85 | 7632 | 100514 | 401058 | 0.39901 | 8767200 | 364038 | 0.041523 | 846365 | 130427.6864 | 765096 | 154103.3554 | 5.8661
85-86 | 7852 | 91852 | 328917 | 0.35809 | 8611200 | 361161 | 0.041941 | 846365 | 121233.4144 | 690078 | 143240.1085 | 5.6921
86-87 | 6238 | 86956 | 186058 | 0.21397 | 8407200 | 330664 | 0.039331 | 846365 | 115641.3664 | 516722 | 136632.9732 | 4.4683
87-88 | 7138 | 98071 | 235637 | 0.24027 | 8894600 | 376025 | 0.042276 | 846865 | 128419.3752 | 611662 | 151640.9052 | 4.763
88-89 (1) | 7817 | 100426 | 231792 | 0.23081 | 9900000 | 418470 | 0.04227 | 846365 | 134204.8 | 650262 | 158566.1033 | 4.8453
89-90 (2) | 8181 | 99062 | 232017 | 0.23421 | 9614400 | 431765 | 0.044908 | 938865 | 131866.3328 | 663782 | 140452.9222 | 5.0337
90-91 (3) | 7795 | 98739 | 251671 | 0.25489 | 10459200 | 463053 | 0.044272 | 944865 | 134425.7904 | 714724 | 142269.8379 | 5.3169
91-92 | 7915 | 92268 | 159770 | 0.17316 | 10699200 | 473973 | 0.0443 | 944865 | 128773.6704 | 633743 | 136287.904 | 4.9214
92-93 (4) | 7296 | 95977 | 165834.46 | 0.17279 | 10420800 | 480192 | 0.044 | 966865 | 131532.7696 | 646026.46 | 136040.4706 | 4.9115
93-94 | 7098 | 85173 | 212107.05 | 0.24903 | 10384173 | 487721.55 | 0.046968 | 972865 | 120603.7983 | 699828.6 | 123967.6608 | 5.8027
94-95 | 6139 | 77444 | 155666.62 | 0.20101 | 10454200 | 509883.07 | 0.048773 | 972865 | 113113.7304 | 665550 | 116268.6811 | 5.8839
95-96 | 7921 | 91589 | 211776 | 0.23122 | 10836825 | 531950.66 | 0.049087 | 972865 | 128564.2469 | 743726 | 132149 | 5.7849
96-97 | 7297 | 99991 | 293146.26 | 0.29317 | 11983679 | 559179.31 | 0.046662 | 1018615 | 140879.3127 | 852325.57 | 139404 | 5.8647
97-98 | 6589 | 82412 | 223641.54 | 0.27137 | 12782400 | 613894 | 0.048027 | 1056615 | 126025.5488 | 837535.54 | 119272.9128 | 6.6458
98-99 | 6788 | 86690 | 197452.77 | 0.22777 | 12972000 | 626697 | 0.048312 | 1056615 | 130950.464 | 824149.77 | 123933.9438 | 6.2936
99-00 | 6669 | 76959 | 221394 | 0.28768 | 12117600 | 621699 | 0.051305 | 1053903 | 118370 | 843093 | 112315.8393 | 7.1225
00-01 | 7959 | 94701 | 506962 | 0.53533 | 11611968 | 567550.07 | 0.048876 | 1149717 | 134321.0348 | 1074512.07 | 116829.6501 | 7.9996
01-02 | 6681 | 85416 | 326532 | 0.38228 | 12739200 | 640022.43 | 0.05024 | 1187717 | 128882.1504 | 966554.43 | 108512.5079 | 7.4995
02-03 | 7787 | 91334 | 432449.78 | 0.47348 | 13257600 | 637913.79 | 0.048117 | 1187717 | 136568.9312 | 1070363.57 | 114984.4039 | 7.8375
03-04 | 7433 | 89501 | 423755 | 0.47346 | 12969600 | 639256.44 | 0.049289 | 1187717 | 133753.2752 | 1063011.44 | 112613.7583 | 7.9476
04-05 | 7161 | 107579.2115 | 461911 | 0.42937 | 12944171 | 677250.68 | 0.052 | 1208213 | 151744.7229 | 1139161.68 | 125594.3471 | 7.5071
05-06 | 6545 | 78282.15 | 715475.742 | 0.91397 | 13058757 | 807129.35 | 0.061808 | 1208213 | 122838.6289 | 1522605.092 | 101669.6798 | 12.3952
06-07 | 7082 | 77067 | 469784 | 0.60958 | 12399200 | 836588 | 0.067471 | 1208213 | 119373.0704 | 1306372 | 98801.3458 | 10.9436
07-08 | 7914 | 89275 | 785994 | 0.88042 | 10787257 | 796219 | 0.073811 | 1208213 | 126081.1209 | 1582213 | 104353.3888 | 12.5492
08-09 | 7743 | 85403 | 514774 | 0.60276 | 12337600 | 947030 | 0.07676 | 1208213 | 127498.8912 | 1461804 | 105526.8328 | 11.4652
09-10 | 7216 | 77752 | 461433 | 0.59347 | 11670400 | 853399 | 0.073125 | 1208213 | 117571.4048 | 1314832 | 97310.1637 | 11.1833
10-11 | 7870 | 80809 | 494775 | 0.61228 | 11887400 | 908134 | 0.076395 | 1208213 | 121368.8088 | 1402909 | 100453.1559 | 11.5591
11-12 | 6302 | 64591 | 316037 | 0.48929 | 11454100 | 903976 | 0.078922 | 1208213 | 103672.3892 | 1220013 | 85806.3845 | 11.768
12-13 | 7562 | 82310 | 393809 | 0.47845 | 11916100 | 979799 | 0.082225 | 1208213 | 122967.7332 | 1373608 | 101776.5354 | 11.1705
1. Library built and on line ('88)
2. Weyerhaeuser Hall renovated--a/c added.
3. Carnegie Hall renovated--a/c added along with more usable area.
4. Humanities renovated--additional space and a/c.
5. Old Main renovated-additional space and A/C ('93-'94)
6. Rice renovation under way--construction heat throughout the year ('95-'96)
7. Rice operational with new mechanical systems, Olin's construction heat supplied by gas kiln meter--not reflected in this report ('96-'97)
8. New Residence Hall put on-line in August 1997. Additional 38,000 square feet of area. First air conditioned residence hall. ('97-'98)
9. Old Dayton Hall and Student Union torn down summer of 1999. Temporary heat for Campus Center Construction ('99-'00)
10. Kagin taken out of operation during January 2001. Campus Center comes on line in January. ('00-'01)
11. Kagin comes back on line January 2002.
12. Sold 1750 Summit and repurchased 1635 Summit as the new President's house. Completed renovation of Wallace Hall. ('03-'04)
13. Completed renovation of Turck Hall. ('04-'05)
14. Demolished Fieldhouse, pool, gym in fall 2006.
15. Winton Health Center demolished June '08 to make way for new Institute for Global Citizenship (IGC) building.
16. New Leonard Center opens August '08
17. New Institute for Global Citizenship (IGC) opens in June '09
18. New Chiller Plant commissioned in June '09
19. Janet Wallace Fine Arts Complex remodel started (Music Building) January 2011
20. Music Building move in, July 2012
21. Art Building remodel and boiler replacement started January 2013
22. Boiler replacement complete, online November 2013
23. ART Building move in, January 2014

## 12-13 Budget
MACALESTER COLLEGE
MONTHLY ENERGY BUDGET REPORT
JUNE 2012 - MAY 2013
| FY 2012/2013 | FY 2012/2013 | Yr. to Date | Yr. to Date | Estimated | Estimated
| Budgeted | Budgeted | 6/1/12 - 5/31/13 | 6/1/12 - 5/31/13 |  |  | FY 2012/2013 | FY 2012/2013
ENERGY | Consumption | Total | Quantity | $ | Quantity | $ | TOTAL | TOTAL
TYPE | (BTUs/KWH) | Expenditure | Consumed | Expenditure | Consumed | Expenditure | CONSUMPTION | EXPENDITURE
GAS (MCF)
- Heating Plant | 800000000 | 424000 | 0 | 0 |  |  | 77910 | 351968
- All other blds | 124000000 | 106250
OIL (GAL.)
#6 |  |  | 0 | 0 |  |  | 29332 | 41841
#2 |  |  | 0 | 0
TOTAL BTUs | 924000000 | 530250 | 0 | 0 |  | 0 | 823098000 | 393809
(* 1,000)
ELEC. (KWH)
- Main meter | 12000000 | 996000 | 0 | 0 |  | 0 | 10934700 | 859665
- All other blds | 600000 | 72000 |  |  |  |  | 981400 | 120133
- Contingency |  | 0
Total ELEC. | 12600000 | 1068000 |  |  |  |  | 11916100 | 979798
TOTAL
EXPENDED | 964944000 | 530250 | 0 | 0 |  |  | 863755733.2 | 1373607
Variance:
[6 empty] | Budget -vs- Estimate |  | -843357
Fuel Variance:
[6 empty] | Consumption |  | -57903.9886
[6 empty] | Price |  | -78537.0114
[6 empty] | Sub-Total |  | -136441
Electrical Variance:
[6 empty] | Consumption |  | -88419.9
[6 empty] | Price |  | -47915.1
[6 empty] | Sub-Total |  | -136335
Total Variance
[6 empty] | Fuel & Electrical |  | -272776

## HDD vs Consump Stats
YEAR | HEATING | CONSUMED | FUEL | COST | KWH | ELECTRIC | COST | SQUARE | BTU | BTU | CONSUMP | per
| HDD | x1,000,000 | COST | PER | CONSUMED | COST | PER | FEET | CONSUM | COST | BTU/SQ FT | X1000K
90-91 | 7795 | 98739 | 251671 | 0.25489 | 10459200 | 463053 | 0.044272 | 944865 | 134425.7904 | 714724 | 142269.8379 | 5.3169
91-92 | 7915 | 92268 | 159770 | 0.17316 | 10699200 | 473973 | 0.0443 | 944865 | 128773.6704 | 633743 | 136287.904 | 4.9214
92-93 | 7296 | 95977 | 165834.46 | 0.17279 | 10420800 | 480192 | 0.044 | 966865 | 131532.7696 | 646026.46 | 136040.4706 | 4.9115
93-94 | 7098 | 85173 | 212107.05 | 0.24903 | 10384173 | 487721.55 | 0.046968 | 972865 | 120603.7983 | 699828.6 | 123967.6608 | 5.8027
94-95 | 6139 | 77444 | 155666.62 | 0.20101 | 10454200 | 509883.07 | 0.048773 | 972865 | 113140 | 665550 | 116295.6834 | 5.8825
95-96 | 7921 | 91589 | 211776 | 0.23122 | 10836825 | 531950.66 | 0.049 | 972865 | 128564 | 743726 | 132149 | 5.7849
96-97 | 7297 | 99991 | 293146.26 | 0.29317 | 11983679 | 559179.31 | 0.049 | 1018615 | 140880 | 852325.57 | 139404 | 5.8647
97-98 | 6589 | 82412 | 223641.54 | 0.27137 | 12782400 | 613894 | 0.048 | 1056615 | 120632 | 837535.54 | 114168.3584 | 6.9429
98-99 | 6806 | 86670 | 199452 | 0.23013 | 12972000 | 626697 | 0.048 | 1056615 | 131330 | 826149 | 124293.1437 | 6.2906
99-00 | 6698 | 77025 | 221699 | 0.28783 | 12117600 | 621699 | 0.051305 | 1053903 | 118370 | 843398 | 112315.8393 | 7.1251
00-01 | 7959 | 94701 | 506962 | 0.53533 | 11611968 | 567550.07 | 0.048876 | 1149717 | 134321.0348 | 1074512.07 | 116829.6501 | 7.9996
01-02 | 6681 | 85416 | 326532 | 0.38228 | 12739200 | 640022.43 | 0.05024 | 1187717 | 128882.1504 | 966554.43 | 108512.5079 | 7.4995
02-03 | 7787 | 91334 | 432449.78 | 0.47348 | 13257600 | 637913.79 | 0.048117 | 1187717 | 136568.9312 | 1070363.57 | 114984.4039 | 7.8375
03-04 | 7433 | 89501 | 423755.16 | 0.47346 | 12969600 | 639256.44 | 0.049289 | 1187717 | 133753.2752 | 1063011.6 | 112613.7583 | 7.9476
04-05 | 7161 | 107579.2115 | 461911 | 0.42937 | 12944171 | 677250.68 | 0.052 | 1208213 | 151744.7229 | 1139161.68 | 125594.3471 | 7.5071
05-06 | 6545 | 78282.15 | 715475.742 | 0.91397 | 13058757 | 807129.35 | 0.061808 | 1208213 | 122838.6289 | 1522605.092 | 101669.6798 | 12.3952
06-07 | 7082 | 77067 | 469764 | 0.60955 | 11177000 | 770180 | 0.068908 | 1208213 | 115202.924 | 1239944 | 95349.8464 | 10.7631
07-08 | 7914 | 89275 | 785994 | 0.88042 | 10787257 | 796219 | 0.073811 | 1208213 | 126081.1209 | 1582213 | 104353.3888 | 12.5492
08-09 | 7743 | 85403 | 514774 | 0.60276 | 12337600 | 947030 | 0.07676 | 1208213 | 127498.8912 | 1461804 | 105526.8328 | 11.4652
09-10 | 7216 | 77753 | 461433 | 0.59346 | 11670400 | 853400 | 0.073125 | 1208213 | 117572.4048 | 1314833 | 97310.9914 | 11.1832
10-11 | 7870 | 80810 | 494770 | 0.61226 | 11887400 | 908134 | 0.076395 | 1208213 | 121369.8088 | 1402904 | 100453.9835 | 11.5589
11-12 | 6302 | 64591 | 316037 | 0.48929 | 11454100 | 903976 | 0.078922 | 1208213 | 103672.3892 | 1220013 | 85806.3845 | 11.768
12-13 | 7562 | 82310 | 393810 | 0.47845 | 11916100 | 979799 | 0.082225 | 1208213 | 122967.7332 | 1373609 | 101776.5354 | 11.1705
YEAR | HEATING | Btus | Cost of Fuel | Cost of Fuel
| Heating Degree Days | x10,000,000 | x10 | x100
90-91 | 7795 | 9873.9 | 25167.1 | 2516.71
91-92 | 7915 | 9226.8 | 15977 | 1597.7
92-93 | 7296 | 9597.7 | 16583.446 | 1658.3446
93-94 | 7098 | 8517.3 | 21210.705 | 2121.0705
94-95 | 6139 | 7744.4 | 15566.662 | 1556.6662
95-96 | 7921 | 9158.9 | 21177.6 | 2117.76
96-97 | 7297 | 9999.1 | 29314.626 | 2931.4626
97-98 | 6589 | 8241.2 | 22364.154 | 2236.4154
98-99 | 6788 | 8667 | 19945.2 | 1994.52
99-00 | 6669 | 7702.5 | 22169.9 | 2216.99
00-01 | 7959 | 9470.1 | 50696.2 | 5069.62
01-02 | 6681 | 8541.6 | 32653.2 | 3265.32
02-03 | 7787 | 9133.4 | 43244.978 | 4324.4978
03-04 | 7433 | 8950.1 | 42375.516 | 4237.5516
04-05 | 7161 | 10757.9211 | 46191.1 | 4619.11
05-06 | 6545 | 7828.215 | 71547.5742 | 7154.7574
06-07 | 7082 | 7828.215 | 71547.5742 | 7154.7574
07-08 | 7914 | 8927.5 | 78599.4 | 7859.94
08-09 | 7743 | 8540.3 | 51477.4 | 5147.74
09-10 | 7216 | 7775 | 46143 | 4614.3
10-11 | 7870 | 8081 | 49477 | 4947.7
11-12 | 6302 | 6459 | 31604 | 3160.37
12-13 | 7562 | 8231 | 39381 | 3938.1

## Condensate by Bldg
METER READINGS
|  | June |  | July |  | August |  | September |  | October |  | November |  | December |  | January |  | February |  | March |  | April |  | May | Annual
| 2012-07-01 |  | 2012-08-01 |  | 2012-09-01 |  | 2012-10-01 |  | 2012-11-01 |  | 2012-12-03 |  | 2013-01-02 |  | 2013-02-03 |  | 2013-03-01 |  | 2013-04-01 |  | 2013-05-01 |  | 2013-06-01 |  |  | %
| READING | UNITS | READING | UNITS | READING | UNITS | READING | UNITS | READING | UNITS | READING | UNITS | READING | UNITS | READING | UNITS | READING | UNITS | READING | UNITS | READING | UNITS | READING | UNITS | TOTAL
ART & POWER PLANT | 7532350 | 0 | 7532350 | 0 | 7532350 | 0 | 7538810 | 6460 | 7602390 | 63580 | 7719270 | 116880 | 7924340 | 205070 | 8157390 | 233050 | 8343320 | 185930 | 8484840 | 141520 | 8589300 | 104460 | 8589300 | 0 | 915430 | 10.01%
CARNEGIE | 2137170 | 0 | 2137170 | 0 | 2137170 | 0 | 2137210 | 40 | 2143230 | 6020 | 2156850 | 13620 | 2176800 | 19950 | 2191550 | 14750 | 2199470 | 7920 | 2204540 | 5070 | 2206460 | 1920 | 2206460 | 0 | 64220 | 0.7022%
OLD MAIN | 1635870 | 0 | 1635870 | 0 | 1635870 | 0 | 1635870 | 0 | 1638480 | 2610 | 1643930 | 5450 | 1661100 | 17170 | 1680550 | 19450 | 1681720 | 1170 | 1681840 | 120 | 1681840 | 0 | 1681840 | 0 | 45850 | 0.5013%
LIBRARY | 2950130 | 0 | 2950130 | 0 | 2950130 | 0 | 2954680 | 4550 | 2996960 | 42280 | 3043600 | 46640 | 3075070 | 31470 | 3077540 | 2470 | 3077540 | 0 | 3077540 | 0 | 3077540 | 0 | 3077540 | 0 | 127410 | 1.393%
WEYERHAEUSER HALL | 2317180 | 0 | 2317180 | 0 | 2317180 | 0 | 2334740 | 17560 | 2362700 | 27960 | 2393800 | 31100 | 2434280 | 40480 | 2479860 | 45580 | 2521610 | 41750 | 2560310 | 38700 | 2591790 | 31480 | 2591790 | 0 | 235910 | 2.579%
CHAPEL | 802230 | 0 | 802230 | 0 | 802230 | 0 | 811990 | 9760 | 823170 | 11180 | 840260 | 17090 | 865690 | 25430 | 890500 | 24810 | 915670 | 25170 | 935910 | 20240 | 951370 | 15460 | 951370 | 0 | 128900 | 1.409%
BIGELOW | 3485120 | 0 | 3485120 | 0 | 3485120 | 0 | 3500970 | 15850 | 3515460 | 14490 | 3538210 | 22750 | 3569860 | 31650 | 3573040 | 3180 | 3587500 | 14460 | 3588190 | 690 | 3589800 | 1610 | 3589800 | 0 | 103990 | 1.137%
WALLACE & 30 MAC | 8095720 | 0 | 8095720 | 0 | 8095720 | 0 | 8097270 | 1550 | 8118510 | 21240 | 8153540 | 35030 | 8197310 | 43770 | 8242730 | 45420 | 8295650 | 52920 | 8340210 | 44560 | 8371410 | 31200 | 8371410 | 0 | 231130 | 2.527%
GD DAYTON | 2686300 | 0 | 2686300 | 0 | 2686300 | 0 | 2688000 | 1700 | 2703300 | 15300 | 2729500 | 26200 | 2765400 | 35900 | 2802800 | 37400 | 2839900 | 37100 | 2873000 | 33100 | 2895600 | 22600 | 2895600 | 0 | 176200 | 1.927%
DOTY | 383810 | 0 | 383810 | 0 | 383810 | 0 | 389110 | 5300 | 421380 | 32270 | 475520 | 54140 | 534080 | 58560 | 588380 | 54300 | 655010 | 66630 | 723570 | 68560 | 779900 | 56330 | 779900 | 0 | 327530 | 3.581%
TURCK | 2776930 | 0 | 2776930 | 0 | 2776930 | 0 | 2777540 | 610 | 2793700 | 16160 | 2827380 | 33680 | 2879960 | 52580 | 2936430 | 56470 | 2995490 | 59060 | 3045120 | 49630 | 3078970 | 33850 | 3078970 | 0 | 252410 | 2.76%
DUPRE | 7272460 | 0 | 7272460 | 0 | 7272460 | 0 | 7277700 | 5240 | 7309520 | 31820 | 7361870 | 52350 | 7427250 | 65380 | 7477490 | 50240 | 7527470 | 49980 | 7548270 | 20800 | 7562470 | 14200 | 7562470 | 0 | 269210 | 2.944%
KAGIN | 2467240 | 0 | 2467240 | 0 | 2467240 | 0 | 2469520 | 2280 | 2487520 | 18000 | 2515260 | 27740 | 2558760 | 43500 | 2606490 | 47730 | 2648670 | 42180 | 2684430 | 35760 | 2706500 | 22070 | 2706500 | 0 | 203500 | 2.225%
MARKIM HALL | [16 empty] | . | [6 empty] | 0
CAMPUS CENTER | 9390200 | 0 | 9390200 | 0 | 9390200 | 0 | 9440300 | 50100 | 1999990 | 510000 | 1999990 | 650000 | 1999990 | 660000 | 31690 | 440000 | 92670 | 60980 | 146130 | 53460 | 201840 | 55710 | 201840 | 0 | 2394280 | 26.18%
KIRK | 9700 | 0 | 9700 | 0 | 9700 | 0 | 12130 | 2430 | 33780 | 21650 | 70950 | 37170 | 119490 | 48540 | 167670 | 48180 | 214340 | 46670 | 254840 | 40500 | 278040 | 23200 | 278040 | 0 | 252399 | 2.76%
LEONARD CENTER | 2756660 | 0 | 2756660 | 0 | 2756660 | 0 | 2812633 | 55973 | 2892571 | 79938 | 2983231 | 90660 | 3073702 | 90471 | 3175486 | 101784 | 3282554 | 107068 | 3365943 | 83389 | 3413702 | 47759 | 3413702 | 0 | 726094 | 7.939%
RICE | 23043400 | 0 | 23043400 | 0 | 23043400 | 0 | 23051900 | 8500 | 23176400 | 124500 | 23384600 | 208200 | 23858200 | 473600 | 24573600 | 715400 | 25139200 | 565600 | 25474100 | 334900 | 25674300 | 200200 | 25674300 | 0 | 2095800 | 22.92%
MUSIC | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  | 0 | 0 | 0%
HUMANITIES | 6998900 | 0 | 6998900 | 0 | 6998900 | 0 | 7019450 | 20550 | 7042090 | 22640 | 7093440 | 51350 | 7221400 | 127960 | 7296550 | 75150 | 7296560 | 10 | 7296560 | 0 | 7296560 | 0 | 7296560 | 0 | 297660 | 3.255%
DISTRICT HEATING | 3367610 | 0 | 3367610 | 0 | 3367610 | 0 | 3368650 | 1040 | 3378480 | 9830 | 3394930 | 16450 | 3416010 | 21080 | 3438910 | 22900 | 3459750 | 20840 | 3478470 | 18720 | 3491990 | 13520 | 3491990 | 0 | 105660 | 1.155%
THEATER | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 40300 | 40300 | 98630 | 58330 | 158390 | 59760 | 213710 | 55320 | 247590 | 33880 | 247590 | 0 | 192270 | 2.102%
| 90108980 | 0 | 90108980 | 0 | 90108980 | 0 | 90318473 | 209493 | 83439631 | 1071468 | 84326131 | 1536500 | 85798992 | 2132861 | 85487286 | 2096594 | 86932484 | 1445198 | 87977523 | 1045039 | 88686972 | 709449 | 88686972 | 0 | 9145853 | 100%

## Electrical Read by Bldg
LOCATION | May | JUNE |  | JULY |  | AUGUST |  | SEPTEMBER |  | OCTOBER |  | NOVEMBER |  | DECEMBER |  | JANUARY |  | FEBRUARY |  | MARCH |  | APRIL |  | MAY |  | ANNUAL | % OF
READ DATE | 2012-06-05 | 2012-07-02 |  | 2012-08-01 |  | 2012-09-04 |  | 2012-10-01 |  | 2012-11-01 |  | 2012-12-03 |  | 2013-01-02 |  | 2013-02-03 |  | 2013-03-01 |  | 2013-04-01 |  | 2013-05-01 |  | 2013-05-31
| Reading | Reading | Total | Reading | Total | Reading | Total | Reading | Total | Reading | Total | Reading | Total | Reading | Total | Reading | Total | Reading | Total | Reading | Total | Reading | Total | Reading | Total | TOTAL | CAMPUS
MUSIC (PB1) |  |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 0%
ART LIGHTS (TC) |  |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 0%
THEATER (TA) |  |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 0%
MUSIC LIGHTS (TB) |  |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 0%
CARNEGIE |  |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 0%
POWER PLANT |  |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 0%
CHILLER (Xcel meter) | 3192319 | 3384649 | 192330 | 3700394 | 315745 | 3911421 | 211027 | 3984527 | 73106 | 4001197.75 | 16670.75 | 4004255.5 | 3057.75 | 4007365 | 3109.5 | 4011019 | 3654 | 4018127.5 | 7108.5 | 4027495.5 | 9368 | 4031080 | 3584.5 | 4086031 | 54951 | 893712 | 3.507%
LIBRARY (minus OM, Kirk) | 7080 | 7267 | 37580 | 7485 | 41960 | 7702 | 46600 | 7941 | 49660 | 8251 | 65660 | 8559 | 61960 | 8846 | 55580 | 9110 | 49360 | 9424 | 61660 | 9736 | 60740 | 48 | 65420 | 272 | 49620 | 645800 | 2.534%
OLD MAIN | 66341 | 66806 | 9300 | 67380 | 11480 | 67994 | 12280 | 68639 | 12900 | 69452 | 16260 | 70354 | 18040 | 71519 | 23300 | 72739 | 24400 | 73896 | 23140 | 75043 | 22940 | 76012 | 19380 | 76603 | 11820 | 205240 | 0.8054%
CHAPEL | 40372 | 40639 | 8010 | 40890 | 7530 | 41085 | 5850 | 41259 | 5220 | 41567 | 9240 | 41925 | 10740 | 42270 | 10350 | 42590 | 9600 | 42954 | 10920 | 43311 | 10710 | 43637 | 9780 | 43848 | 6330 | 104280 | 0.4092%
BIGELOW | 6068 | 6237 | 10140 | 6442 | 12300 | 6685 | 14580 | 6938 | 15180 | 7237 | 17940 | 7558 | 19260 | 7963 | 24300 | 8362 | 23940 | 8799 | 26220 | 9227 | 25680 | 9519 | 17520 | 9709 | 11400 | 218460 | 0.8573%
WEY HALL | 68424 | 68746 | 6440 | 69124 | 7560 | 69534 | 8200 | 69859 | 6500 | 70271 | 8240 | 70685 | 8280 | 71157 | 9440 | 71666 | 10180 | 72173 | 10140 | 72661 | 9760 | 73080 | 8380 | 73184 | 2080 | 95200 | 0.3736%
WALLACE | 1746311 | 1755631 | 69900 | 1764753 | 68415 | 1776365 | 87090 | 1789003 | 94785 | 1803892 | 111667.5 | 1819726 | 118755 | 1831129 | 85522.5 | 1842184 | 82912.5 | 1856360 | 106320 | 1860383 | 30172.5 | 1874519 | 106020 | 1874519 | 0 | 961560 | 3.773%
DOTY | 72711 | 73110 | 11970 | 73589 | 14370 | 74157 | 17040 | 74718 | 16830 | 75435 | 21510 | 76172 | 22110 | 76733 | 16830 | 77252 | 15570 | 77913 | 19830 | 78613 | 21000 | 79296 | 20490 | 79707 | 12330 | 209880 | 0.8236%
TURCK | 39798 | 40007 | 3135 | 40264 | 3855 | 40564 | 4500 | 40949 | 5775 | 41410 | 6915 | 41891 | 7215 | 42241 | 5250 | 42533 | 4380 | 42967 | 6510 | 43394 | 6405 | 43821 | 6405 | 44131 | 4650 | 60495 | 0.2374%
30 MAC | 4754 | 5409 | 4912.5 | 6132 | 5422.5 | 6980 | 6360 | 7868 | 6660 | 8907 | 7792.5 | 10002 | 8212.5 | 10856 | 6405 | 11666 | 756075 | 12606 | 7050 | 13571 | 7237.5 | 14505 | 7005 | 15151 | 4845 | 821617.5 | 3.224%
GD DAYTON | 5795635 | 5812446 | 16811 | 5833538 | 21092 | 5856831 | 23293 | 5879504 | 22673 | 5906787 | 27283 | 5934646 | 27859 | 5973246 | 38600 | 6012397 | 39151 | 6055493 | 43096 | 6096063 | 40570 | 6120745 | 24682 | 6141293 | 20548 | 345658 | 1.356%
DUPRE | 3434122 | 3445975 | 11853 | 3459281 | 13306 | 3482070 | 22789 | 3509719 | 27649 | 3541325 | 31606 | 3576329 | 35004 | 3603806 | 27477 | 3627738 | 23932 | 3660316 | 32578 | 3692749 | 32433 | 3724172 | 31423 | 3747016 | 22844 | 312894 | 1.228%
KAGIN (minus Markim Hall) | 3143237 | 3163397 | 116422.016 | 3185167 | 117403.031 | 3210949 | 120517.089 | 3234938 | 119157.614 | 3260869 | 120209.625 | 3284832 | 118478.828 | 3305967 | 116235.641 | 3326951 | 116015.78 | 3351203 | 118256.939 | 3373064 | 116325.25 | 3398199 | 119658.159 | 3420535 | 117529.747 | 1416209.719 | 5.557%
MARKIM HALL | 193828.672 | 197566.656 | 3737.984 | 201933.625 | 4366.969 | 207198.536 | 5264.911 | 212029.922 | 4831.386 | 217751.297 | 5721.375 | 223235.469 | 5484.172 | 228134.828 | 4899.359 | 233103.048 | 4968.22 | 239098.109 | 5995.061 | 244633.859 | 5535.75 | 250110.7 | 5476.841 | 254916.953 | 4806.253 | 61088.281 | 0.2397%
CAMPUS CENTER | 12266 | 85230 | 172964 | 69397 | 84167 | 68097.9 | 98700.9 | 66072.6 | 97974.7 | 80803.5 | 114730.9 | 95748 | 114944.5 | 89428.9 | 93680.9 | 85493.1 | 96064.2 | 99259.5 | 113766.4 | 8372.6 | 9113.1 | 15505 | 107132.4 | 13368 | 97863 | 1201102 | 4.713%
KIRK | 2303 | 2384 | 12960 | 2486 | 16320 | 2552 | 10560 | 2639 | 13920 | 2747 | 17280 | 2863 | 18560 | 2944 | 12960 | 3011 | 10720 | 3109 | 15680 | 3210 | 16160 | 3304 | 15040 | 3368 | 10240 | 170400 | 0.6687%
LEONARD CENTER | 6717473 | 7018264 | 300791 | 7387010 | 368746 | 7774378 | 387368 | 8095494 | 321116 | 8460510 | 365016 | 8830968 | 370458 | 9149919 | 318951 | 9503626 | 353707 | 9883623 | 379997 | 241122 | 357499 | 605999 | 364877 | 840313 | 234314 | 4122840 | 16.18%
MAIN VAULT (Xcel meter) | 14336 | 14658 | 676200 | 15037 | 795900 | 15448 | 863100 | 15834 | 810600 | 16299 | 976500 | 16781 | 1012200 | 17226 | 934500 | 17670 | 932400 | 18167 | 1043700 | 18646 | 1005900 | 19108 | 970200 | 19473 | 766500 | 10787700 | 42.33%
STADIUM | 71225 | 71311 | 8600 | 71394 | 8300 | 71521 | 12700 | 71622 | 10100 | 72086 | 46400 | 72833 | 74700 | 74006 | 117300 | 75275 | 126900 | 76519 | 124400 | 77490 | 97100 | 78156 | 66600 | 78395 | 23900 | 717000 | 2.814%
RICE | 34678908 | 34833436 | 154528 | 35014014 | 180578 | 35189239 | 175225 | 35336727 | 147488 | 35500832 | 164105 | 35666241 | 165409 | 35816468 | 150227 | 35958387 | 141919 | 36116319 | 157932 | 36275395 | 159076 | 36438282 | 162887 | 36592419 | 154137 | 1913511 | 7.509%
HUM POW & LIG | 43953 | 44404 | 13530 | 44965 | 16830 | 45633 | 20040 | 46221 | 17640 | 46968 | 22410 | 47697 | 21870 | 48266 | 17070 | 48808 | 16260 | 49442 | 19020 | 50069 | 18810 | 50731 | 19860 | 51253 | 15660 | 219000 | 0.8594%
SUBTOTAL |  |  | 1842114.5 |  | 2115646.5 |  | 2153084.9 |  | 1879765.7 |  | 2173157.65 |  | 2242597.75 |  | 2071987.9 |  | 2842108.7 |  | 2333319.9 |  | 2062535.1 |  | 2151820.9 |  | 1626368 | 25483647.5 | 100%
MAIN & CHILLER METERS | as read by MAC |  | 868530 |  | 1111645 |  | 1074127 |  | 883706 |  | 993170.75 |  | 1015257.75 |  | 937609.5 |  | 936054 |  | 1050808.5 |  | 1015268 |  | 973784.5 |  | 821451 | 11681412
TOTAL |  |  | 973584.5 |  | 1004001.5 |  | 1078957.9 |  | 996059.7 |  | 1179986.9 |  | 1227340 |  | 1134378.4 |  | 1906054.7 |  | 1282511.4 |  | 1047267.1 |  | 1178036.4 |  | 804917 | 13802235.5
MAIN & CHILLER METERS - Xcel | from Xcel | * | 812000 | # | 1013600 |  | 978600 |  | 975100 |  | 963200 |  | 918400 |  | 1080100 |  | 1021300 |  | 1008000 |  | 968800 |  | 947800 |  | 856100 | 11543000
% OF MAIN & CHILLER METERS |  |  | 119.9% |  | 99.05% |  | 110.3% |  | 102.1% |  | 122.5% |  | 133.6% |  | 105% |  | 186.6% |  | 127.2% |  | 108.1% |  | 124.3% |  | 94.02% | 119.6%
* June total does not include any chiller plant usage
Difference between MAC readings and Xcel readings - Kwh | [6 empty] | 95527 |  | -91394 |  | 29970.75 |  | 96857.75 |  | -142490.5 |  | -85246 |  | 42808.5 |  | 46468 |  | 25984.5 |  | -34649 | 138412
Percentage | [6 empty] | 109.8% |  | 90.63% |  | 103.1% |  | 110.5% |  | 86.81% |  | 91.65% |  | 104.2% |  | 104.8% |  | 102.7% |  | 95.95% | 101.2%

## Wind Turbine Data
2012-13 | Month
Day | June | July | Aug. | Sept. | Oct. | Nov. | Dec. | Jan. | Feb. | March | April | May
1 | 32.05 | 0.015 | 0 | 0.33 | 0 | 0.103 | 1.651 | 0 | 2.09 | 2.487 | 2.93 | 5.48
2 | 8.15 | 1.156 | 2.908 | 0.996 | 3.835 | 3.571 | 4.587 | 0.136 | 12.24 | 1.446 | 9.92 | 9.6
3 | 0 | 3.714 | 1.622 | 1.439 | 0.033 | 0.001 | 1.274 | 0.067 | 15.39 | 0 | 4.31 | 3.49
4 | 0 | 2.808 | 2.869 | 0 | 0.91 | 0 | 8.652 | 2.261 | 0.12 | 1.691 | 0.31 | 1.25
5 | 2.56 | 2.045 | 2.828 | 0.515 | 29.446 | 0.003 | 6.448 | 2.164 | 8.73 | 4.904 | 2.71 | 1.35
6 | 0.95 | 0.185 | 2.934 | 1.904 | 21.751 | 0.933 | 13.433 | 0.507 | 0.49 | 1.416 | 1.89 | 0.25
7 | 0.02 | 3.635 | 0.341 | 0.047 | 4.293 | 5.04 | 8.196 | 1.32 | 3.09 | 0.457 | 3.09 | 1.37
8 | 0.79 | 2.062 | 0.398 | 7.673 | 2.641 | 0.044 | 0 | 5.011 | 3.91 | 0.593 | 3.91 | 2.92
9 | 0.02 | 0.126 | 1.08 | 13.876 | 3.351 | 2.816 | 0.09 | 2.74 | 9.23 | 2.175 | 9.23 | 0
10 | 5.64 | 1.102 | 3.83 | 0.02 | 9.967 | 5.022 | 5.859 | 9.477 | 4.6 | 1.545 | 4.6 | 0.58
11 | 2.51 | 0 | 1.203 | 11.274 | 1.897 | 11.465 | 2.445 | 4.106 | 0.88 | 13.532 | 0.88 | 11.86
12 | 2.98 | 0.349 | 0 | 13.491 | 7.568 | 9.804 | 4.72 | 2.51 | 12.08 | 5.333 | 12.08 | 5.11
13 | 0.19 | 3.21 | 0 | 1.333 | 3.905 | 10.29 | 4.15 | 18.728 | 1.91 | 10.822 | 1.91 | 0.02
14 | 0.51 | 3.885 | 0.986 | 0.841 | 1.725 | 0.354 | 8.99 | 0.223 | 1.14 | 1.121 | 0 | 0.08
15 | 0.58 | 0.294 | 0 | 0 | 5.375 | 0 | 2.08 | 0.203 | 0.542 | 0.106 | 2.18 | 4.81
16 | 1.18 | 0.003 | 2.757 | 3.373 | 0.637 | 1.14 | 3.14 | 5.028 | 9.449 | 0.374 | 1.29 | 12.82
17 | 1.01 | 10.309 | 13.16 | 3.089 | 1.525 | 0.542 | 12.41 | 6.891 | 10.671 | 2.719 | 6.54 | 4.68
18 | 0.04 | 0.836 | 0.048 | 4.357 | 7.057 | 9.449 | 0.39 | 0.706 | 1.904 | 3.216 | 0.3 | 0.4
19 | 0.08 | 1.455 | 0.001 | 0.575 | 0.002 | 10.671 | 11.53 | 3.892 | 0.047 | 25.134 | 4.51 | 2.72
20 | 0.99 | 0 | 0.165 | 10.862 | 0.002 | 0.912 | 2.56 | 25.266 | 7.673 | 22.877 | 0.89 | 2.78
21 | 2.79 | 0.682 | 0 | 6.019 | 0.11 | 0.058 | 8.29 | 8.03 | 13.876 | 16.144 | 0.51 | 21.97
22 | 12.93 | 0.582 | 0.041 | 5.12 | 2.188 | 2.313 | 0 | 10.079 | 0.02 | 0.011 | 17 | 13.44
23 | 0.07 | 0.148 | 1.509 | 10.519 | 2.971 | 18.837 | 2.59 | 0.428 | 6.745 | 0 | 7.673 | 0.92
24 | 1.01 | 0.526 | 3.439 | 1.426 | 1.244 | 26.883 | 3.54 | 12.893 | 0.285 | 0 | 13.876 | 6.7
25 | 0 | 0.674 | 4.557 | 4.71 | 2.233 | 0.403 | 0.27 | 1.345 | 0.125 | 2.378 | 0.02 | 6.5
26 | 0.032 | 2.243 | 0.321 | 0.06 | 20.118 | 4.568 | 0.02 | 11.656 | 0.018 | 3.55 | 11.274 | 0
27 | 6.572 | 4.62 | 0 | 0.09 | 6.745 | 1.738 | 3.11 | 0.716 | 1.039 | 0.046 | 13.491 | 2.09
28 | 3.127 | 0.802 | 0.001 | 0 | 0.285 | 0.89 | 7.98 | 0.994 | 0.841 | 0.017 | 1.333 | 12.24
29 | 1.476 | 0.176 | 0.905 | 0 | 0.125 | 0.692 | 13.48 | 0.159 |  | 0.011 | 0.841 | 0.56
30 | 0.094 | 0.055 | 2.987 | 0.004 | 0.018 | 0.929 | 7.58 | 4.167 |  | 1.016 | 0.125 | 8.46
31 |  | 1.781 | 3.751 |  | 1.039 |  | 0.81 | 0 |  | 1.792 |  | 5.6
Total | 88.351 | 49.478 | 54.641 | 103.943 | 142.996 | 129.471 | 150.275 | 141.703 | 129.135 | 126.913 | 139.623 | 150.05 | 1406.579

## Fuel Cost Comparisons
Heating Fuel Cost Comparisons - 2012/13
| Sept | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | AVG.
Quoted Price
Natural Gas - $/MCF |  | 3.7686 | 4.3864 | 4.4445 | 4.0351 | 4.018 | 4.0891 | 4.7096 | 4.9275
#2 Fuel Oil - $/Gal |  | 3.268 | 3.1835 | 3.221 | 3.166 | 3.047 | 3.54 | 3.635 | 3.635
#6 Fuel Oil - $/Gal | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Fuel Used |  | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS
Comparitive Price per Million BTUs
Natural Gas | 0 | 4.5958 | 5.3493 | 5.4201 | 4.9208 | 4.9 | 4.9867 | 5.7434 | 6.0091
#2 Fuel Oil | 0 | 27.3385 | 26.6316 | 26.9453 | 26.4852 | 25.4897 | 29.6139 | 30.4086 | 30.4086
#6 Fuel Oil | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
NOTE: The costs expressed are for 1,000,000 btus. The unit price of each fuel is converted to reflect the cost
to burn 1 million btus of each fuel type.
Premium to Burn Gas vs. #6 Fuel Oil
Total BTU's
QTY-BTU (x 1000) | Nov: NOTE: #6 fuel oil use discontinued Spring 2013; AVG.: 0
YTD Cost
Nat. Gas @ $x.xx/mil BTU's= | 0 | 0 | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | #REF!
#6 Fuel Oil @ $x.xx/mil BTU's= | #VALUE! | #VALUE! | #REF! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
YTD Savings
Premium to burn gas= | #VALUE! | #VALUE! | #REF! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #REF!